## CO2
Carbon Dioxide Gas Room Capacity Calculation
(CO2)
Not to be used for asphyxiant gases (N2,Ar,He) please see other sheet
Click here for more information on the risks on CO2
Full Bottle Release Scenario
Specific vol @ room temperature, 1 atm (m3/kg) (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Details for RA Calculations' to assist) |  | Specific Volume @ 15°C atm |  | Mass of cylinder contents (kg) |  |  |  | CO2 Concentration (%)
| * | 0.5531 |  |  | * |  |  | #DIV/0!
*must have a value inputted |  | Specific volume increases as room temp. increases. At 25°C, the specific volume is approx. 0.5531... m3/kg. At 30°C the specific volume is approx. 0.5625… m3/kg."
The cylinder volume/size can be found on the neck of the cylinder or on the BOC website. Common bottle sizes and volumes are also listed in the "Bottle Sizes" tab.
Click here for HSE guidance on Workplace Exposure Limits
Timed Release Scenario Calculation
Free volume of the laboratory/room (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Information' to assist) |  | Volume of CO2 released (m³/hr) |  | Air changes per hour |  | Known Duration of Leak. (Hours) |  | CO2 Concentration (%) after known timing of leakage
94.51 | * | 1.2 | * | 1.3 | * | 1 | * | 0.70697
*must have a value inputted |  | 1.2 m³/hr is considered to be a reasonable assumtion for a slow leak in gas connections. A more detailed calculation can be found at: https://lenoxlaser.com/capabilities/orifice-calculator/ |  | This is the how many times the air in a room is fully replaced with fresh air per hour. Information on the air change rate for each laboratory/room can be found in the "Room Information" tab.
Slow Release Scenario Calculation
Free volume of the laboratory/room (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Information' to assist) |  | Volume of CO2 released (m³/hr) |  | Air changes per hour |  |  |  | CO2 Concentration (%) after indefinte time of leakage
94.51 | * | 1.2 |  | 1.3 | * |  |  | 0.96725
*must have a value inputted |  | 1.2 m³/hr is considered to be a reasonable assumtion for a slow leak in gas connections. A more detailed calculation can be found at: https://lenoxlaser.com/capabilities/orifice-calculator/ |  | This is the how many times the air in a room is fully replaced with fresh air per hour. Information on the air change rate for each laboratory/room can be found in the "Room Information" tab.
Note on J21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I have here =D21/(B21*F21+D21)*100; in cell J19 'CO2 concentration after long periods (days)'; cell F23 'This is the how many times the air in a room is fully replaced with fresh air per hour. Information on the air change rate for each lab can be found in the "Room Information" tab.' Reply: The solution for CO2 concentration after 1 hr of leakage should be a more complex expression. See BCGA GN11 rev4. p 22.
Note on J35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I have here =D21/(B21*F21+D21)*100; in cell J19 'CO2 concentration after long periods (days)'; cell F23 'This is the how many times the air in a room is fully replaced with fresh air per hour. Information on the air change rate for each lab can be found in the "Room Information" tab.' Reply: The solution for CO2 concentration after 1 hr of leakage should be a more complex expression. See BCGA GN11 rev4. p 22.
If over 0.5% CO2 monitors must be in place before work starts.
(for periods of less than 15min 1.5%)
If over 0.5% CO2 monitors must be in place before work starts.
(for periods of less than 15min 1.5%)
If over 0.5% CO2 monitors must be in place before work starts.
(for periods of less than 15min 1.5%)

## Inert gas
Asphyxiant Gas Room Capacity Calculation
(Nitrogen, Argon, Helium)
Not to be used for Oxygen or Carbon Dioxide, please see other sheet
Click here for more information on the risks of inert gases
Full Bottle Release Scenario
Free volume of the laboratory/room (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Information' to assist) |  | Volume of Gas (m³) @15°C atm | OR | Bottle size Litres |  | Oxygen concentration (%)
| * |  | * |  | * | #DIV/0! | #DIV/0!
*must have a value inputted
|  | The cylinder volume/size can be found on the neck of the cylinder or on the BOC website. Common bottle sizes and volumes are also listed in the "Bottle Sizes" tab. |  | Bottle pressure (bar)@15°C
Click here for HSE guidance on Workplace Exposure Limits
*
Slow Release Scenario Calculation
Free volume of the laboratory/room (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Information' to assist) |  | Volume of gas released (m³/hr) |  | Air changes per hour |  | O2 Concentration (%) after indeterminate length of leakage
| * |  | * |  | * | #DIV/0!
*must have a value inputted |  | 1.2 m³/hr is considered to be a reasonable assumtion for a slow leak in gas connections. A more detailed calculation can be found at: https://lenoxlaser.com/capabilities/orifice-calculator/ |  | This is the how many times the air in a room is fully replaced with fresh air per hour. Information on the air change rate for each laboratory/room can be found in the "Room Information" tab.
Note on I21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I think the function in cell I23 is for O2 concentration after long periods (days).
Note on I23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Do you want to change 0.209 to 0.2095? It changes the third sig fig. in the example I did.
If less than 19.5% Oxygen monitors must be in place before work starts
If less than 19.5% Oxygen monitors must be in place before work starts

## Oxygen
Oxygen Enrichment Room Capacity Calculation
(O2)
Not to be used for asphyxiant gases or Carbon Dioxide, please see other sheet
Click here for more information on the risks of Oxygen
Full Bottle Release Scenario
Free volume of the laboratory/room (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Information' to assist) |  | Volume of Gas (m³) @ 15°C atm | OR | Bottle size Litres |  | Oxygen concentration (%)
| * |  | * |  | *
*must have a value inputted
The cylinder volume/size can be found on the neck of the cylinder or on the BOC website. Common bottle sizes and volumes are also listed in the "Bottle Sizes" tab. |  |  |  | Bottle pressure (bar) @15°C
Click here for HSE guidance on Workplace Exposure Limits
*
Slow Release Scenario Calculation
Free volume of the laboratory/room (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Information' to assist) |  | Volume of gas released (m³/hr) |  | Air changes per hour |  | O2 Concentration (%) after indeterminate length of leakage
| * |  |  |  | * | #DIV/0! | #VALUE!
*must have a value inputted |  | 1.2 m³/hr is considered to be a reasonable assumtion for a slow leak in gas connections. A more detailed calculation can be found at: https://lenoxlaser.com/capabilities/orifice-calculator/ |  | This is the how many times the air in a room is fully replaced with fresh air per hour. Information on the air change rate for each laboratory/room can be found in the "Room Information" tab.
Note on J9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Maybe change 0.21 to 0.2095.
Note on J23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solution in Parker for O2 enrichment predicts O2 concentration of 0 if air exchange rate is 0. In my version I changed this equation to =(0.2095*F23*B23+D23)/(F23*B23+D23)*100 Please find published solution from independent source. Reply: I forgot to mention that the equation above is O2 conc % after long periods (days) of leakage.
If over 23.5% Oxygen monitors must be in place before work starts
If over 23.5% Oxygen monitors must be in place before work starts

## Liquid N2
Cryogenic Liquid Room Capacity Calculation
(Liquid Nitrogen Only)
Not to be used for other cryogenic liquid. Please see chemical technicans and/or local instructions
Click here for more information on the risks of inert gases
Free volume of the laboratory/room (this should be measured in cubic meters and take in to consideration any large objects that reduce the laboratory/rooms' air volume)(m³) (Use 'Room Information' to assist) |  | Capacity of tank (L) |  | Expansion Ratio @ 20°C | Oxygen concentration (%)
300 | * | 25 | * | 694 | 19.7384
*must have a value inputted
The cylinder volume/size can be found on the neck of the cylinder or on the BOC website. Common bottle sizes and volumes are also listed in the "Bottle Sizes" tab.
Click here for HSE guidance on Workplace Exposure Limits
Note on B6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Here and in other spreadsheets change 'the laboratory' to 'the laboratory/room'.
Note on F6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Maybe change to 20 degC; expansion ratio 695?
Note on H8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I have = (B8-(D8*F8)/1000)*0.2095/B8*100
If less than 19.5% Oxygen monitors must be in place before work starts

## Room Information
Laboratory | FVAS m3 (Free Volume of Air in the Lab/Room) | Gas H/S is House supply | Gas volume for risk calculation- Flow ph or total cylinder volume if less than max flow | HVAC rate (Air Changes Per Hour) | Volume of gas per air change | Total gas volume M3 for BOX calculation (ex H/S) | BOX calculation showing worst case scenario for cylinder gases ex H/S | O2 % depletion Without HVAC - conditional criteria | GN11 Calc O2% depletion With HVAC | Alarm activation duration without HVAC to 1st alarm O2 depletion - implies need a gas alarm system | Alarm activation duration without HVAC to 2nd alarm O2 depletion - 30 min(1800secs) rule implies needing a interlock | O2 % enrichment Without HVAC - conditional criteria | GN11 Calc O2% enrichment With HVAC | Alarm activation duration without HVAC to 1st alarm O2 enrichment - implies need a gas alarm system | Flam % without HVAC - conditional criteria = LEL of gas | GN11 Calc Flam % with HVAC | Alarm activation duration without HVAC to 1st alarm LEL - implies need a gas alarm system | Alarm activation duration without HVAC to 2nd alarm LEL - 30 min rule implies needing a interlock | Toxic % without HVAC - conditional criteria = STEL of gas | GN11 Calc Toxic % with HVAC | Alarm activation duration without HVAC to 1st alarm STEL - implies need a gas alarm system | Alarm activation duration without HVAC to 2nd alarm STEL - 30 min rule implies needing a interlock | gas Alarm installed Y/N | gas alarm set point criteria | 1st alarm levels % gas or oxygen | 2nd alarm levels % gas or oxygen | Gas detection recommended Y/N E -existing | Gas Interlock recommended linked to gas detection Y/N | Comments and actions | HVAC essential to maintain safe working environment Y/N
Meston |  |  |  | Ind Min @4
G62 | 272.62 | helium | 10 | 4 | 2.5 | 10 | 20.13 | 20.13 | 20.81 | 1472.15 | 3925.73 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N | Air Changes Per Hour A measure of the air volume added to or removed from a room in one hour. This is periodically measured and calculated by staff then figures updated on this document. It is a measure of how efficient the room’s ventilation is and can be used within slow leak gas calculations. Flow Rate (m3/hour) = (Area of Duct (m2) x Velocity (m/s)) x 3600 Air Changes Per Hour = Flow Rate (m3/hour) Room Volume (m3)
G62 | 272.62 | nitrogen x3 | 15 | 4 | 3.75 | 45 | 17.45 | 19.75 | 20.72 | 981.43 | 2617.15 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G62 | 272.62 | 5%O2/he | 0.5 | 4 | 0.13 | 10 | 24.62 | 20.17 | 20.99 | 29442.96 | 78514.56 | 21.13 | 20.99 | 40238.71 | [8 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G62 | 272.62 | 5%H2/N2 | 0.5 | 4 | 0.13 | 0.5 | 0.18 | 20.17 | 20.99 | 29442.96 | 78514.56 |  |  |  | 0.18 | 0.05 | 15702.91 | 31405.82 |  |  |  |  | N | O2 depletion | 19.5 | 17 | N | N |  | N
G62 | 272.62 | CO2 | 18.5 | 4 | 4.63 | 18.5 | 6.79 | [11 empty] | 6.79 | 1.67 | 212.2 | 424.4 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G62 | 272.62 | 20%CO/He | 2 | 4 | 0.5 | 2 | 0.73 | 20.29 | 20.96 | 7360.74 |  |  |  |  | 0.73 | 0.18 | 3925.73 | 7851.46 | 0.73 | 0.18 | 1962.86 | 3925.73 | Y | STEL and LTEL | 0.002 | 0.01 | E | N |  | Y
G62 | 272.62 | 5%ethyleneN2 | 0.4 | 4 | 0.1 | 0.4 | 0.15 | [7 empty] | 0.15 | 0.04 | 19628.64 | 39257.28 |  |  |  |  | N | 20%LEL and 40%EL | 0.55 | 1.1 | N | N |  | N
G62 | 272.62 | CO2 | 10 | 4 | 2.5 | 10 | 3.67 | [11 empty] | 3.67 | 0.91 | 392.57 | 785.15 | N | STEL and LTEL | 0.5 | 1.5 | Y | N |  | Y
G62 | 272.62 | helium | 2 | 4 | 0.5 | 2 | 20.75 | 20.75 | 20.96 | 7360.74 | 19628.64 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G62 | 272.62 | LN2 | 17 | 4 | 4.25 | 17 | 19.6 | 19.6 | 20.68 | 865.97 | 2309.25 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G62 | 272.62 | Hydrogen | 7.21 | 4 | 1.8 | 7.21 | 2.64 | [7 empty] | 2.64 | 0.66 | 1088.97 | 2177.94 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | N | Calculations show the risk is above the alarm levels, however, they are below the LEL for the gas. Gas detection advised | Y
G62 | 272.62 | methane | 0.2 | 4 | 0.05 | 0.2 | 0.07 | [7 empty] | 0.07 | 0.02 | 39257.28 | 78514.56 |  |  |  |  | N | 20%LEL and 40%EL | 1 | 2 | N | N |  | N
G62 | 272.62 | 300ppmCO/N2 | 0.00012 | 4 | 0 | 0.00012 | 0 | [7 empty] | 0 | 0 | 65428800 | 130857600 | 0 | 0 | 32714400 | 65428800 | N | O2 depletion | 19.5 | 17 | N | N |  | N
G62 | 272.62 | 20%CO2/N2 | 0.09 | 4 | 0.02 | 0.09 | 0.03 | [11 empty] | 0.03 | 0.01 | 43619.2 | 87238.4 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
G62 | 272.62 | CO2 | 2 | 4 | 0.5 | 2 | 0.73 | [11 empty] | 0.73 | 0.18 | 1962.86 | 3925.73 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | Y
G68 | 165.9 | propane | 2.2 | 4 | 0.55 | 2.2 | 1.33 | [7 empty] | 1.33 | 0.33 | 2171.78 | 4343.56 |  |  |  |  | N | 20%LEL and 40%EL | 0.4 | 0.8 | Y | N | Calculations show the risk is above the alarm levels, however, they are below the LEL for the gas. Gas detection advised | Y
G68 | 165.9 | hydrogen | 7.21 | 4 | 1.8 | 7.21 | 4.35 | [7 empty] | 4.35 | 1.07 | 662.68 | 1325.36 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | Y |  | Y
G68 | 165.9 | CO | 10 | 4 | 2.5 | 18 | 10.85 | [7 empty] | 6.03 | 1.48 | 477.79 | 955.58 | 6.03 | 1.48 | 238.9 | 477.79 | N | 20%LEL and 40%EL | 2.5 | 5 | Y | Y |  | Y
G68 | 165.9 | 200ppmH2 | 0.02 | 4 | 0.01 | 0.02 | 0.01 | [7 empty] | 0.01 | 0 | 238896 | 477792 |  |  |  |  | N | O2 depletion | 19.5 | 17 | N | N |  | N
G68 | 165.9 | Hydrogen | 7.21 | 4 | 1.8 | 7.21 | 4.35 | [7 empty] | 4.35 | 1.07 | 662.68 | 1325.36 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | N |  | Y
G68 | 165.9 | oxygen x2 | 10 | 4 | 2.5 | 20 | 33.01 |  |  |  |  | 26.98 | 20.69 | 1224.34 | [8 empty] | N | O2 enrichment | 23 | na | Y | N |  | Y
G68 | 165.9 | LN2 | 17 | 4 | 4.25 | 17 | 18.76 | 18.76 | 20.48 | 526.98 | 1405.27 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N | O2 depletion is below the O2 deficient level of 19.5%, detection is advised due to the risk of spilliage from the liquid N2 | Y
G59 | 175.6 | hydrogen | 7.21 | 4 | 1.8 | 7.21 | 4.11 | [7 empty] | 4.11 | 1.02 | 701.43 | 1402.85 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | N |  | Y
G59 | 175.6 | Argon | 15 | 4 | 3.75 | 15 | 19.11 | 19.11 | 20.56 | 632.16 | 1685.76 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G58 | 108.89 | Oxygen | 15 | 4 | 3.75 | 15 | 34.73 |  |  |  |  | 34.73 | 20.3 | 535.74 | [8 empty] | N | O2 enrichment | 23 | na | Y | N |  | Y
G58 | 108.89 | CO2 | 0.5 | 4 | 0.13 | 0.5 | 0.46 | [11 empty] | 0.46 | 0.11 | 3136.03 | 6272.06 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
G58 | 108.89 | CO2 x2 | 18.2 | 4 | 4.55 | 36.4 | 33.43 | [11 empty] | 16.71 | 4.01 | 86.15 | 172.31 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G66 | 30.42 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 59.83 | [11 empty] | 59.83 | 13.01 | 24.07 | 48.14 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G82 | 40.4 | N2 | 2 | 4 | 0.5 | 2 | 19.87 | 19.87 | 20.74 | 1090.8 | 2908.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G82 | 40.4 | Argon | 2 | 4 | 0.5 | 2 | 19.87 | 19.87 | 20.74 | 1090.8 | 2908.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G82raman | 34.75 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 52.37 | [11 empty] | 52.37 | 11.58 | 27.49 | 54.99 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G79 | 137.02 | Nitrogen x 2 | 15 | 4 | 3.75 | 30 | 16.32 | 18.61 | 20.44 | 493.27 | 1315.39 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G79 | 137.02 | Argon | 15 | 4 | 3.75 | 15 | 18.61 | 18.61 | 20.44 | 493.27 | 1315.39 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G70 | 54.16 | Hydrogen | 7.21 | 4 | 1.8 | 7.21 | 13.31 | [7 empty] | 13.31 | 3.22 | 216.34 | 432.68 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | Y |  | Y
G70 | 54.16 | nitrogen | 15 | 4 | 3.75 | 15 | 15.11 | 15.11 | 19.64 | 194.98 | 519.94 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G74 | 117.98 | hydrogen x 4 | 7.21 | 4 | 1.8 | 28.84 | 24.44 | [7 empty] | 6.11 | 1.5 | 471.27 | 942.53 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | Y |  | Y
G74 | 117.98 | argon | 15 | 4 | 3.75 | 15 | 18.24 | 18.24 | 20.35 | 424.73 | 1132.61 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G74 | 117.98 | nitrogen | 15 | 4 | 3.75 | 15 | 18.24 | 18.24 | 20.35 | 424.73 | 1132.61 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G60 | 26.35 | Argon | 15 | 2.96 | 5.07 | 15 | 9 | 9 | 17.61 | 94.86 | 252.96 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
G78&78A | 82.05 | 5%h2/N2 | 0.5 | 4 | 0.13 | 0.5 | 0.61 | [7 empty] | 0.61 | 0.15 | 4726.08 | 9452.16 |  |  |  |  | N | O2 depletion | 19.5 | 17 | N | N |  | N
G78&78A | 82.05 | CO2 x2 | 18.2 | 4 | 4.55 | 36.4 | 44.36 | [11 empty] | 22.18 | 5.25 | 64.92 | 129.84 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G72 | 53.48 | Argon | 15 | 4 | 3.75 | 15 | 15.04 | 15.04 | 19.62 | 192.53 | 513.41 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G94 | 60.15 | nitrogen | 15 | 4 | 3.75 | 15 | 15.69 | 15.69 | 19.77 | 216.54 | 577.44 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G93 | 55.64 | nitrogen | 2.3 | 4 | 0.58 | 2.3 | 20.04 | 20.04 | 20.79 | 1306.33 | 3483.55 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G93 | 55.64 | Argon | 15 | 4 | 3.75 | 15 | 15.27 | 15.27 | 19.67 | 200.3 | 534.14 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G106 | 54.91 | argon | 15 | 4 | 3.75 | 15 | 15.19 | 15.19 | 19.66 | 197.68 | 527.14 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G102 | 55.25 | Argon | 15 | 4 | 3.75 | 15 | 15.23 | 15.23 | 19.67 | 198.9 | 530.4 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G102 | 55.25 | Nitrogen | 15 | 4 | 3.75 | 15 | 15.23 | 15.23 | 19.67 | 198.9 | 530.4 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G105 | 55 | Argon | 15 | 4 | 3.75 | 15 | 15.2 | 15.2 | 19.66 | 198 | 528 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G92 | 425.59 | Argon x 5 | 15 | 4 | 3.75 | 75 | 17.22 | 20.16 | 20.82 | 1532.12 | 4085.66 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G92 | 425.59 | hydrogen | 7.21 | 4 | 1.8 | 7.21 | 1.69 | [7 empty] | 1.69 | 0.42 | 1700 | 3400 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | N | N |  | Y
G92 | 425.59 | ammonia | 24.65 | 4 | 6.16 | 24.65 | 5.79 | [11 empty] | 5.79 | 1.43 | 248.62 | 497.24 | N | STEL and LTEL | 0.0025 | 0.0035 | Y | Y |  | Y
O83 | 97.78 | argon | 30 | 4 | 7.5 | 30 | 14.49 | 14.49 | 19.5 | 176 | 469.34 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
O82 | 205.6 | nitrogen | 15 | 4 | 3.75 | 15 | 19.38 | 19.38 | 20.62 | 740.16 | 1973.76 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
O82 | 205.6 | liquid nitrogen | 68.3 | 4 | 17.08 | 68.3 | 13.96 | 13.96 | 19.39 | 162.55 | 433.48 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
O82 | 205.6 | bruker 600 | 91.5 | 4 | 22.88 | 91.5 | 11.6 | 11.6 | 18.9 | 121.34 | 323.57 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
O82 | 205.6 | bruker 600 | 66 | 4 | 16.5 | 66 | 14.19 | 14.19 | 19.44 | 168.22 | 448.58 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
O82 | 205.6 | bruker400 | 72.4 | 4 | 18.1 | 72.4 | 13.54 | 13.54 | 19.3 | 153.35 | 408.93 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
O82 | 205.6 | bruker 400 | 72.4 | 4 | 18.1 | 72.4 | 13.54 | 13.54 | 19.3 | 153.35 | 408.93 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
O79 | 220.16 | Helium | 10 | 4 | 2.5 | 10 | 19.95 | 19.95 | 20.76 | 1188.86 | 3170.3 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O79 | 220.16 | Nitrogen | 15 | 4 | 3.75 | 15 | 19.48 | 19.48 | 20.65 | 792.58 | 2113.54 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O79 | 220.16 | nitrogen | 15 | 4 | 3.75 | 15 | 19.48 | 19.48 | 20.65 | 792.58 | 2113.54 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O83a | 73.9 | hydrogen | 7.21 | 4 | 1.8 | 7.21 | 9.76 | [7 empty] | 9.76 | 2.38 | 295.19 | 590.38 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | Y |  | Y
O83a | 73.9 | helium | 10 | 4 | 2.5 | 10 | 18.07 | 18.07 | 20.31 | 399.06 | 1064.16 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
O83a | 73.9 | helium | 10 | 4 | 2.5 | 10 | 18.07 | 18.07 | 20.31 | 399.06 | 1064.16 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
O83a | 73.9 | argon | 2.74 | 4 | 0.69 | 2.74 | 20.13 | 20.13 | 20.81 | 1456.42 | 3883.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O83a | 73.9 | helium | 2.74 | 4 | 0.69 | 2.74 | 20.13 | 20.13 | 20.81 | 1456.42 | 3883.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O83a | 73.9 | hydrogen | 8.8 | 4 | 2.2 | 8.8 | 11.91 | [7 empty] | 11.91 | 2.89 | 241.85 | 483.71 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | Y |  | Y
O83a | 73.9 | 20%oxygen/argon mix | 2 | 4 | 0.5 | 0.08 | 20.88 | 20.33 | 20.86 | 1995.3 | 5320.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O84 | 73.9 | argon | 15 | 4 | 3.75 | 15 | 16.66 | 16.66 | 19.99 | 266.04 | 709.44 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
O89 | 147.1 | carbon dioxide LW | 18.2 | 4 | 4.55 | 18.2 | 12.37 | [11 empty] | 12.37 | 3 | 116.39 | 232.77 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y |  | Y
O89 | 147.1 | liquid nitrogen | 34.15 | 4 | 8.54 | 34.15 | 23.22 | 16.05 | 19.85 | 232.6 | 620.28 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
B61 | 72.9 | Argon | 15 | 4 | 3.75 | 15 | 16.6 | 16.6 | 19.97 | 262.44 | 699.84 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
B61 entry | 19.3 | Argon | 11.5 | 4 | 2.88 | 11.5 | 8.45 | 8.45 | 18.28 | 90.63 | 241.67 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
B53 entry | 31.9 | Argon | 11.5 | 4 | 2.88 | 11.5 | 13.37 | 13.37 | 19.26 | 149.79 | 399.44 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
B53 entry | 39.41 | nitrogen | 15 | 4 | 3.75 | 15 | 12.95 | 12.95 | 19.18 | 141.88 | 378.34 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
165 | 1010.57 | hydrogen | 7.21 | 4 | 1.8 | 7.21 | 0.71 | [7 empty] | 0.71 | 0.18 | 4036.67 | 8073.35 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | N | N |  | Y
165 | 1010.57 | nitrogen | 15 | 4 | 3.75 | 15 | 20.59 | 20.59 | 20.92 | 3638.05 | 9701.47 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
165 | 1010.57 | comp air | 11.5 | 4 | 2.88 | 11.5 | NA | [15 empty] | N | NA
O28a | 62.7 | nitrogen | 15 | 4 | 3.75 | 15 | 15.9 | 15.9 | 19.82 | 225.72 | 601.92 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
O28a | 62.7 | argon | 2 | 4 | 0.5 | 2 | 20.23 | 20.23 | 20.83 | 1692.9 | 4514.4 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O28 | 113.1 | carbon monoxide | 10.5 | 4 | 2.63 | 10.5 | 9.28 | [7 empty] | 9.28 | 2.27 | 310.22 | 620.43 | 9.28 | 2.27 | 155.11 | 310.22 | N | STEL and LTEL | 100ppm | 20ppm | Y | Y |  | Y
O28 | 113.1 | hydrogen | 2 | 4 | 0.5 | 2 | 1.77 | [7 empty] | 1.77 | 0.44 | 1628.64 | 3257.28 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | N | Calculations show the risk is above the alarm levels, however, they are below the LEL for the gas. Gas detection advised | Y
O28 | 113.1 | propane | 2.16 | 4 | 0.54 | 2.16 | 1.91 | [7 empty] | 1.91 | 0.48 | 1508 | 3016 |  |  |  |  | N | 20%LEL and 40%EL | 0.4 | 0.8 | Y | N | Calculations show the risk is above the alarm levels, however, they are below the LEL for the gas. Gas detection advised | Y
O28 | 113.1 | argon | 2 | 4 | 0.5 | 2 | 20.53 | 20.53 | 20.91 | 3053.7 | 8143.2 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O18 | 117.3 | comp air | 11.5 | 4 | 2.88 | 11.5 | NA | [15 empty] | NA | NA
O24 | 84.55 | argon | 15 | 4 | 3.75 | 15 | 17.19 | 17.19 | 20.11 | 304.38 | 811.68 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
O27 | 277.5 | propane | 10.26 | 4 | 2.57 | 10.26 | 3.7 | [7 empty] | 3.7 | 0.92 | 778.95 | 1557.89 |  |  |  |  | N | 20%LEL and 40%EL | 0.4 | 0.8 | Y | N |  | Y
O27 | 287.5 | oxygen | 2 | 4 | 0.5 | 2 | 21.65 |  |  |  |  | 21.65 | 20.96 | 10608.75 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
O28b | 57.36 | liquid nitrogen | 20.49 | 4 | 5.12 | 20.49 | 13.43 | 13.43 | 19.28 | 151.17 | 403.12 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
O19a | 58.8 | carbon dioxide LW | 18.2 | 4 | 4.55 | 38.4 | 65.31 | [11 empty] | 30.95 | 7.18 | 46.52 | 93.05 | Y | STEL and LTEL | 0.5 | 1.5 | Y | Y | very hot room. Relocate to exterior loading are just outside. Incubators are excempt from requireing an interlock | Y
119B | 149.9 | oxygen | 15 | 4 | 3.75 | 15 | 30.96 |  |  |  |  | 30.96 | 20.49 | 737.51 | [8 empty] | N | O2 enrichment | 23 | na | Y | Y |  | Y
119B | 149.9 | comp air | 11.5 | 4 | 2.88 | 11.5 | NA | [15 empty] | N | NA
119B | 149.9 | nitrogen | 15 | 4 | 3.75 | 15 | 18.81 | 18.81 | 20.49 | 539.64 | 1439.04 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
119B | 149.9 | nitrogen | 10 | 4 | 2.5 | 10 | 19.51 | 19.51 | 20.66 | 809.46 | 2158.56 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
119B | 149.9 | carbon dioxide LW | 18.2 | 4 | 4.55 | 18.2 | 12.14 | [11 empty] | 12.14 | 2.95 | 118.6 | 237.2 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
119B | 149.9 | helium | 15 | 4 | 3.75 | 15 | 18.81 | 18.81 | 20.49 | 539.64 | 1439.04 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
119B | 149.9 | helium | 2 | 4 | 0.5 | 2 | 20.62 | 20.62 | 20.93 | 4047.3 | 10792.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
124 | 101.2 | nitrogen | 15 | 4 | 3.75 | 15 | 17.8 | 17.8 | 20.25 | 364.32 | 971.52 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
119 | 125.4 | 10%co2 5%h2 n2 | 1 | 4 | 0.25 | 1 | 0.8 | [11 empty] | 0.8 | 0.2 | 1805.76 | 3611.52 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | Y
119 | 125.4 | 10%co2 5%h2 n2 | 0.5 | 4 | 0.13 | 0.5 | 0.4 | [7 empty] | 0.4 | 0.1 | 7223.04 | 14446.08 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | N | N |  | Y
119 | 125.4 | 10%co2 5%h2 n2 | 8.5 | 4 | 2.13 | 8.5 | 19.48 | 19.48 | 20.65 | 796.66 | 2124.42 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
119 | 125.4 | carbon dioxide | 18.2 | 4 | 4.55 | 18.2 | 14.51 | [11 empty] | 14.51 | 3.5 | 99.22 | 198.44 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
125 | 117.3 | nitrogen | 15 | 4 | 3.75 | 15 | 18.23 | 18.23 | 20.35 | 422.28 | 1126.08 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G06 | 23.32 | nitrogen | 15 | 4 | 3.75 | 15 | 7.46 | 7.46 | 18.09 | 83.95 | 223.87 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
G08 | 201.5 | liquid nitrogen | 25.9 | 4 | 6.48 | 25.9 | 18.21 | 18.21 | 20.35 | 420.12 | 1120.31 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G08 | 201.5 | 2.5%CO2/Argon | 0.25 | 4 | 0.06 | 0.25 | 0.12 | [11 empty] | 0.12 | 0.03 | 11606.4 | 23212.8 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
G08 | 201.5 | 2.5%CO2/Argon | 9.75 | 4 | 2.44 | 9.75 | 19.89 | 19.89 | 20.75 | 1116 | 2976 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
Zoology |  |  |  | Ind Min @4
B33 | 90.1 | CO2 | 18.2 | 4 | 4.55 | 36.4 | 40.4 | [11 empty] | 20.2 | 4.81 | 71.29 | 142.58 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
B33 | 90.1 | Oxygen | 10 | 4 | 2.5 | 10 | 32.05 |  |  |  |  | 32.05 | 20.43 | 664.94 | [8 empty] | N | O2 enrichment | 23 | na | Y | Y |  | Y
B33 | 90.1 | Helium | 10 | 4 | 2.5 | 10 | 18.58 | 18.58 | 20.43 | 486.54 | 1297.44 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
B33 | 90.1 | LN2 | 17 | 4 | 4.25 | 17 | 16.96 | 16.96 | 20.05 | 286.2 | 763.2 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
B31 | 73.84 | LN2 | 41 | 4 | 10.25 | 41 | 9.3 | 9.3 | 18.44 | 97.25 | 259.34 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | 600mm extract fan near ceiling | Y
105 | 29.65 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 61.38 | [11 empty] | 61.38 | 13.3 | 23.46 | 46.92 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
113 | 90.61 | Nitrogen | 10 | 4 | 2.5 | 10 | 18.59 | 18.59 | 20.44 | 489.29 | 1304.78 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
229 | 25.5 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 71.37 | [11 empty] | 71.37 | 15.14 | 20.18 | 40.35 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
228 | 28.72 | nitrogen | 10 | 4 | 2.5 | 10 | 13.62 | 13.62 | 19.32 | 155.09 | 413.57 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
325 | 24.65 | oxygen | 10 | 4 | 2.5 | 10 | 61.52 |  |  |  |  | 61.52 | 19.07 | 181.92 | [8 empty] | N | O2 enrichment | 23 | na | Y | Y |  | Y
423 | 28.46 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 63.95 | [11 empty] | 63.95 | 13.78 | 22.52 | 45.04 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
Cruickshanks |  |  |  | Ind Min @4
G16 | 147.22 | helium | 10 | 4 | 2.5 | 20 | 18.06 | 19.48 | 20.65 | 794.99 | 2119.97 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G16 | 147.22 | hydrogen | 7.21 | 4 | 1.8 | 7.21 | 4.9 | [7 empty] | 4.9 | 1.21 | 588.06 | 1176.13 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | N |  | Y
G16 | 147.22 | nitrogen | 10 | 4 | 2.5 | 10 | 19.48 | 19.48 | 20.65 | 794.99 | 2119.97 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G16 | 147.22 | oxygen | 10 | 4 | 2.5 | 18 | 33.18 |  |  |  |  | 27.74 | 20.65 | 1086.48 | [8 empty] | N | O2 enrichment | 23 | na | Y | Y |  | Y
G16 | 147.22 | 10ppmCH4/2.5ppmN2O/0.1%CO2/N2 | 5e-05 | 4 | 1.3e-05 | 5e-05 | 20.95 | [7 empty] | 3e-05 | 1e-05 | 84798720 | 169597440 |  |  |  |  | N | 20%LEL and 40%EL | 1 | 2 | N | N |  | N
G16 | 147.22 | 10ppmCH4/2.5ppmN2O/0.1%CO2/N2 | 1.25e-05 | 4 | 3e-06 | 1.25e-05 | 20.95 |  |  |  |  | 20.95 | 21 | 869186880 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
G16 | 147.22 | 10ppmCH4/2.5ppmN2O/0.1%CO2/N2 | 0.0005 | 4 | 0.000125 | 0.0005 | 20.95 | [11 empty] | 0.0003 | 0.0001 | 4239936 | 8479872 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
G16 | 147.22 | 10ppmCH4/2.5ppmN2O/0.1%CO2/N2 | 0.499 | 4 | 0.12475 | 0.499 | 21.29 | 20.83 | 20.98 | 15931.62 | 42484.33 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G16 | 147.22 | 10ppmN2O/25ppmCH4/0.5%CO2/N2 | 5e-05 | 4 | 1.3e-05 | 5e-05 | 20.95 |  |  |  |  | 20.95 | 21 | 217296720 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
G16 | 147.22 | 10ppmN2O/25ppmCH4/0.5%CO2/N2 | 0.000125 | 4 | 3.1e-05 | 0.000125 | 20.95 | [7 empty] | 0.0001 | 2e-05 | 33919488 | 67838976 |  |  |  |  | N | 20%LEL and 40%EL | 1 | 2 | N | N |  | N
G16 | 147.22 | 10ppmN2O/25ppmCH4/0.5%CO2/N2 | 0.0025 | 4 | 0.000625 | 0.0025 | 20.95 | [11 empty] | 0.0017 | 0.0004 | 847987.2 | 1695974.4 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
G16 | 147.22 | 10ppmN2O/25ppmCH4/0.5%CO2/N2 | 0.497 | 4 | 0.12425 | 0.497 | 21.29 | 20.83 | 20.98 | 15995.73 | 42655.29 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G34 | 81.5 | Argon | 10 | 4 | 2.5 | 10 | 18.34 | 18.34 | 20.38 | 440.1 | 1173.6 | [11 empty] | Y | O2 depletion | 19.5 | 17 | N | N |  | Y
G34 | 81.5 | Nitrogen | 10 | 4 | 2.5 | 30 | 13.21 | 18.34 | 20.38 | 440.1 | 1173.6 | [11 empty] | Y | O2 depletion | 19.5 | 17 | N | N |  | Y
G34 | 81.5 | LN2 120lts | 82 | 4 | 20.5 | 82 | 0.13 | 0.13 | 16.78 | 53.67 | 143.12 | [11 empty] | Y | O2 depletion | 19.5 | 17 | Y | N |  | Y
G34 | 81.5 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 22.33 | [11 empty] | 22.33 | 5.29 | 64.48 | 128.97 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G34 | 81.5 | acetylene manifold | 9.01 | 4 | 2.25 | 9.01 | 11.06 | [7 empty] | 11.06 | 2.69 | 260.51 | 521.02 |  |  |  |  | Y | 20%LEL and 40%EL | 0.4 | 0.8 | Y | Y |  | Y
G34 | 81.5 | Nitrous Oxide manifold | 2 | 4 | 0.5 | 2 | 2.45 |  |  |  |  | 23.4 | 20.87 | 3007.35 | [8 empty] | Y | O2 enrichment | 23 | na | Y | Y |  | Y
G34 | 81.5 | oxygen manifold | 10 | 4 | 2.5 | 10 | 33.22 |  |  |  |  | 33.22 | 20.38 | 601.47 | [8 empty] | Y | O2 enrichment | 23 | na | Y | Y |  | Y
G34 | 81.5 | helium | 10 | 4 | 2.5 | 10 | 18.34 | 18.34 | 20.38 | 440.1 | 1173.6 | [11 empty] | Y | O2 depletion | 19.5 | 17 | N | N |  | Y
G35 | 55.15 | Argon bulk 200lt | 168.4 | 4 | 42.1 | 168.4 | -42.92 | -42.92 | 11.91 | 17.68 | 47.16 | [11 empty] | Y | O2 depletion | 19.5 | 17 | Y | N | Look for a different location or pipe in the gas | Y
G01 | 200.1 | Nitrogen | 10 | 4 | 2.5 | 10 | 19.86 | 19.86 | 20.74 | 1080.54 | 2881.44 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
1.02 | 185.2 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 9.83 | [11 empty] | 9.83 | 2.4 | 146.53 | 293.06 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.01 | 178.9 | CO2 | 18.2 | 4 | 4.55 | 18.2 | 10.17 | [11 empty] | 10.17 | 2.48 | 141.55 | 283.09 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
2.07 | 26.5 | Argon bulk 200lt | 168.4 | 4 | 42.1 | 168.4 | -111.91 | -111.91 | 8.11 | 8.5 | 22.66 | [11 empty] | Y | O2 depletion | 19.5 | 17 | Y | N | Look for a different location or pipe in the gas | Y
2.07 | 26.5 | Nitrogen manifolds in cage | 10 | 4 | 2.5 | 20 | 5.13 | 13.01 | 19.19 | 143.1 | 381.6 | [11 empty] | Y | O2 depletion | 19.5 | 17 | Y | Y |  | Y
Polworth Bld |  |  |  | Ind Min @4
0.019 | 59.1 | 10%CO2/5%O2/N2 | 10 | 4 | 2.5 | 10 | 16.92 | 17.89 | 20.15 | 319.14 | 851.04 | 21.8 | 20.15 | 436.16 |  |  |  |  | 1.69 | 4.06 | 85.1 | 170.21 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | Y
3.02O | 104.3 | CO2 x 3 | 18.2 | 4 | 4.55 | 54.6 | 52.35 | [11 empty] | 17.45 | 4.18 | 82.52 | 165.05 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
4.007 | 66.5 | nitrogen | 6.6 | 4 | 1.65 | 6.6 | 18.83 | 18.83 | 20.49 | 544.09 | 1450.91 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
Rowett Int |  |  |  | Ind Min @4
1.013 | 71.14 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 12.09 | 12.09 | 19 | 128.05 | 341.47 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | one wall open to atmosphere 20.25m2 open | Y
2.019 | 161 | 10%H2/10%CO2/N2 piped 2x1 | 2 | 9.6 | 0.21 | 2 | 1.24 | [7 empty] | 1.24 | 0.13 | 2318.4 | 4636.8 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | N |  | Y
2.019 | 161 | 10%H2/10%CO2/N2 piped 2x1 | 2 | 9.6 | 0.21 | 2 | 1.24 | [11 empty] | 1.24 | 0.13 | 1159.2 | 2318.4 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | Y
2.019 | 161 | 10%H2/10%CO2/N2 piped 2x1 | 16 | 9.6 | 1.67 | 16 | 18.82 | 18.82 | 20.78 | 543.38 | 1449 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
2.019 | 161 | nitrogen x 36 n2 peak generators | 30 | 9.6 | 3.13 | 30 | 17.01 | 17.01 | 20.6 | 289.8 | 772.8 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
2.019 | 161 | Methane piped 1x1 | 10 | 9.6 | 1.04 | 10 | 6.21 | [7 empty] | 6.21 | 0.64 | 463.68 | 927.36 |  |  |  |  | Y | 20%LEL and 40%EL | 1 | 2 | E | Y |  | Y
2.019 | 161 | CO2 piped 230lt | 30 | 9.6 | 3.13 | 123 | 76.4 | [11 empty] | 18.63 | 1.9 | 77.28 | 154.56 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
2.019 | 161 | 10% CO2/90%N2 | 1 | 9.6 | 0.1 | 1 | 0.62 | [11 empty] | 0.62 | 0.06 | 2318.4 | 4636.8 | Y | STEL and LTEL | 0.5 | 1.5 | E | N |  | Y
2.019 | 161 | 10% CO2/90%N2 | 9 | 9.6 | 0.94 | 9 | 19.73 | 19.73 | 20.88 | 966 | 2576 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
2.019 | 161 | 10%CO2/90% O2 | 1 | 9.6 | 0.1 | 1 | 0.62 | [11 empty] | 0.62 | 0.06 | 2318.4 | 4636.8 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | Y
2.019 | 161 | 10%CO2/90% O2 | 9 | 9.6 | 0.94 | 9 | 5.59 |  |  |  |  | 26.54 | 20.88 | 1320.2 | [8 empty] | Y | O2 enrichment | 23 | na | E | N |  | Y
2.019 | 161 | Hydrogen piped 2x1 | 12 | 9.6 | 1.25 | 14.42 | 8.96 | [7 empty] | 7.45 | 0.77 | 386.4 | 772.8 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | Y |  | Y
2.019 | 161 | Hydrogen piped 2x1 | 12 | 9.6 | 1.25 | 14.42 | 8.96 | [7 empty] | 7.45 | 0.77 | 386.4 | 772.8 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | Y |  | Y
2.019 | 161 | Oxygen piped | 10 | 9.6 | 1.04 | 10 | 27.16 |  |  |  |  | 27.16 | 20.87 | 1188.18 | [8 empty] | Y | O2 enrichment | 23 | na | E | Y |  | Y
2.019 | 161 | Helium piped 1x2cyl | 12 | 9.6 | 1.25 | 20 | 18.3 | 19.34 | 20.84 | 724.5 | 1932 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
2.019 | 161 | Argon 240lt piped | 30 | 9.6 | 3.13 | 198 | 4.8 | 17.01 | 20.6 | 289.8 | 772.8 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
2.019 | 161 | Argon 240lt piped | 30 | 9.6 | 3.13 | 198 | 4.8 | 17.01 | 20.6 | 289.8 | 772.8 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
5.001 | 365.8 | CO2 piped 230lt | 30 | 4 | 7.5 | 123 | 33.62 | [11 empty] | 8.2 | 2.01 | 175.58 | 351.17 | N | STEL and LTEL | 0.5 | 1.5 | N | N | into fume hood 0.32m/sec extract | Y
5.001 | 368.5 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 19.2 | 19.2 | 20.58 | 663.3 | 1768.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
5.003 | 96.5 | CO2 piped 230lt | 30 | 4 | 7.5 | 123 | 127.46 | [11 empty] | 31.09 | 7.21 | 46.32 | 92.64 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
5.007 | 114.8 | Hydrogen piped 2x1 | 12 | 7.5 | 1.6 | 14.42 | 12.56 | [7 empty] | 10.45 | 1.37 | 275.52 | 551.04 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | Y |  | Y
5.007 | 114.8 | CO2 piped 230lt | 30 | 7.5 | 4 | 123 | 107.14 | [11 empty] | 26.13 | 3.37 | 55.1 | 110.21 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
5.007 | 114.8 | nitrogen x 36 n2 peak generators | 30 | 7.5 | 4 | 30 | 15.44 | 15.44 | 20.29 | 206.64 | 551.04 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
5.007 | 114.8 | 10%H2/10%CO2/N2 piped 2x1 | 2 | 7.5 | 0.27 | 2 | 1.74 | [7 empty] | 1.74 | 0.23 | 1653.12 | 3306.24 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | N | N |  | Y
5.007 | 114.8 | 10%H2/10%CO2/N2 piped 2x1 | 2 | 7.5 | 0.27 | 2 | 1.74 | [11 empty] | 1.74 | 0.23 | 826.56 | 1653.12 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | Y
5.007 | 114.8 | 10%H2/10%CO2/N2 piped 2x1 | 16 | 7.5 | 2.13 | 16 | 17.99 | 17.99 | 20.62 | 387.45 | 1033.2 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
5.009 | 57.5 | Hydrogen piped 2x1 | 12 | 13.4 | 0.9 | 14.42 | 25.08 | [7 empty] | 20.87 | 1.53 | 138 | 276 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | Y | ceiling | Y
5.009 | 57.5 | nitrogen x 36 n2 peak generators | 30 | 13.4 | 2.24 | 30 | 10 | 10 | 20.21 | 103.5 | 276 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | Y |  | Y
5.009 | 57.5 | CO2 piped 230lt | 30 | 13.4 | 2.24 | 123 | 213.91 | [11 empty] | 52.17 | 3.75 | 27.6 | 55.2 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
5.015 | 54.9 | CO2 piped 230lt | 30 | 15.6 | 1.92 | 123 | 224.04 | [11 empty] | 54.64 | 3.38 | 26.35 | 52.7 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
5.015 | 54.9 | nitrogen 2x4 | 35 | 15.6 | 2.24 | 80 | 9.56 | 7.58 | 20.18 | 84.7 | 225.87 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | Y |  | Y
5.019 | 208.1 | NO GAS |  | 4 | 0 |  | 0 | [15 empty] | Y | O2 depletion | 19.5 | 17 | NA | NA |  | NA
5.027 | 59.9 | CO2 piped 230lt | 30 | 9.5 | 3.16 | 123 | 205.34 | [11 empty] | 50.08 | 5.01 | 28.75 | 57.5 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
5.028 | 109.1 | CO2 piped 230lt | 30 | 8 | 3.75 | 123 | 112.74 | [11 empty] | 27.5 | 3.32 | 52.37 | 104.74 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
5.028 | 109.1 | nitrogen x 36 n2 peak generators | 30 | 8 | 3.75 | 30 | 15.15 | 15.15 | 20.3 | 196.38 | 523.68 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
5.033 | 381.1 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 19.25 | 19.25 | 20.59 | 685.98 | 1829.28 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.32m/sec x2 | Y
4.035 | 381.1 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 19.25 | 19.25 | 20.59 | 685.98 | 1829.28 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.32m/sec | Y
4.034 | 128.5 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 16.02 | 16.02 | 19.84 | 231.3 | 616.8 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.32m/sec x3 | Y
4.03 | 79.43 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 13.01 | 13.01 | 19.19 | 142.97 | 381.26 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.41 m/sec x1 | Y
4.03 | 79.43 | CO2 piped 230lt | 30 | 4 | 7.5 | 123 | 154.85 | [11 empty] | 37.77 | 8.63 | 38.13 | 76.25 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
4.023 | 61.76 | CO2 piped 230lt | 30 | 14.2 | 2.11 | 123 | 199.16 | [11 empty] | 48.58 | 3.31 | 29.64 | 59.29 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
4.022 | 39.42 | CO2 piped 230lt | 30 | 11.3 | 2.65 | 123 | 312.02 | [11 empty] | 76.1 | 6.31 | 18.92 | 37.84 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
4.02 | 207.3 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 17.88 | 17.88 | 20.27 | 373.14 | 995.04 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.31m/3 x 1 | Y
4.019 | 38.34 | nitrogen x 36 n2 peak generators | 30 | 4 | 7.5 | 30 | 4.55 | 4.55 | 17.56 | 69.01 | 184.03 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | Y |  | Y
4.012 | 95.6 | nitrogen x 36 n2 peak generators | 30 | 12.2 | 2.46 | 30 | 14.34 | 14.34 | 20.47 | 172.08 | 458.88 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.31m/sec x 1 | Y
4.011 | 40.8 | nitrogen x 36 n2 peak generators | 30 | 10.4 | 2.88 | 30 | 5.53 | 5.53 | 19.61 | 73.44 | 195.84 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | Y |  | Y
4.011 | 40.8 | CO2 piped 230lt | 30 | 10.4 | 2.88 | 123 | 301.47 | [11 empty] | 73.53 | 6.6 | 19.58 | 39.17 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
4.011 | 40.8 | oxygen piped | 10 | 10.4 | 0.96 | 10 | 45.46 |  |  |  |  | 45.46 | 20.52 | 301.1 | [8 empty] | Y | O2 enrichment | 23 | na | E | Y |  | Y
4.01 | 58.52 | CO2 piped 230lt | 30 | 4 | 7.5 | 123 | 210.18 | [11 empty] | 51.26 | 11.36 | 28.09 | 56.18 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
4.001 | 380.2 | nitrogen x 36 n2 peak generators | 30 | 11.5 | 2.61 | 30 | 19.25 | 19.25 | 20.86 | 684.36 | 1824.96 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.31 m/sec x2 | Y
3.021 | 96.35 | O2/N2 capped | 0 | 12 | 0 | 0 | 0 | [15 empty] | Y | O2 depletion | 19.5 | 17 | E | NA |  | NA
3.021 | 96.35 | O2/N2/CO2 capped | 0 | 12 | 0 | 0 | 0 | [15 empty] | Y | STEL and LTEL | 0.5 | 1.5 | E | NA |  | NA
2.026 | 299 | nitrogen x 36 n2 peak generators | 30 | 11.5 | 2.61 | 30 | 18.8 | 18.8 | 20.82 | 538.2 | 1435.2 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.31m/sec x2 | Y
2.026 | 299 | hydrogen piped 2x1 | 12 | 11.5 | 1.04 | 14.42 | 4.82 | [7 empty] | 4.01 | 0.35 | 717.6 | 1435.2 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | Y |  | Y
2.026 | 299 | CO2/N2 | 10 | 11.5 | 0.87 | 10 | 3.34 | [11 empty] | 3.34 | 0.29 | 430.56 | 861.12 | Y | STEL and LTEL | 0.5 | 1.5 | E | N |  | Y
2.025 | 104.5 | hydrogen piped 2x1 | 12 | 16.5 | 0.73 | 14.42 | 13.8 | [7 empty] | 11.48 | 0.69 | 250.8 | 501.6 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | Y |  | Y
2.025 | 104.5 | Acetylene capped | 0 | 16.5 | 0 | 0 | 0 | [15 empty] | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | NA |  | NA
2.025 | 104.5 | nitrous oxide capped | 0 | 16.5 | 0 | 0 | 0 | [15 empty] | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | NA |  | NA
2.025 | 104.5 | Argon 240lt piped | 30 | 16.5 | 1.82 | 198 | 18.7 | 14.9 | 20.64 | 188.1 | 501.6 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | Y |  | Y
2.025 | 104.5 | Helium piped 1x2cyl | 12 | 16.5 | 0.73 | 20 | 16.9 | 18.5 | 20.85 | 470.25 | 1254 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
2.02 | 346.9 | Oxygen piped | 10 | 4 | 2.5 | 10 | 23.83 |  |  |  |  | 23.83 | 20.85 | 2560.12 | [8 empty] | Y | O2 enrichment | 23 | na | E | N |  | Y
2.02 | 346.9 | Helium piped 1x2cyl | 12 | 4 | 3 | 20 | 19.7 | 20.18 | 20.82 | 1561.05 | 4162.8 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
2.017 | 139.1 | nitrogen x 36 n2 peak generators | 30 | 17.9 | 1.68 | 30 | 16.39 | 16.39 | 20.75 | 250.38 | 667.68 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | fume hood 0.31m/sec x2 | Y
2.014 | 128.9 | nitrogen x 36 n2 peak generators | 30 | 5.5 | 5.45 | 30 | 16.04 | 16.04 | 20.15 | 232.02 | 618.72 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | Y |  | Y
2.014 | 128.9 | Argon 240lt piped | 30 | 5.5 | 5.45 | 198 | 11.2 | 16.04 | 20.15 | 232.02 | 618.72 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | Y |  | Y
2.012 | 192.5 | nitrogen x 36 n2 peak generators | 30 | 5.7 | 5.26 | 30 | 17.64 | 17.64 | 20.44 | 346.5 | 924 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
2.012 | 192.5 | Helium piped 1x2cyl | 12 | 5.7 | 2.11 | 20 | 18.73 | 19.6 | 20.77 | 866.25 | 2310 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
2.012 | 192.5 | Methane piped 1x1 | 10 | 5.7 | 1.75 | 10 | 5.19 | [7 empty] | 5.19 | 0.9 | 554.4 | 1108.8 |  |  |  |  | Y | 20%LEL and 40%EL | 1 | 2 | E | Y |  | Y
2.01 | 61.71 | 10% CO2/90%N2 | 1 | 4 | 0.25 | 10 | 16.2 | [11 empty] | 1.62 | 0.4 | 888.62 | 1777.25 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y |  | Y
2.01 | 61.71 | 10%CO2/90% O2 | 9 | 4 | 2.25 | 11 | 38.78 |  |  |  |  | 35.53 | 20.26 | 506.02 | [8 empty] | Y | O2 & CO2 detection | 19.5 | 17 | E | Y |  | Y
IMS |  |  |  | Ind Min @4
2.46 | 122.47 | CO2 x2 | 12 | 4 | 3 | 36.4 | 29.72 | [11 empty] | 9.8 | 2.39 | 146.96 | 293.93 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
2.5 | 850 | nitrogen | 15 | 4 | 3.75 | 15 | 20.53 | 20.53 | 20.91 | 3060 | 8160 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
2.50:1 | 122.5 | CO2 x2 | 12 | 4 | 3 | 36.4 | 29.71 | [11 empty] | 9.8 | 2.39 | 147 | 294 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
2.54 | 229.73 | CO2 | 12 | 4 | 3 | 18.2 | 7.92 | [11 empty] | 5.22 | 1.29 | 275.68 | 551.35 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
2.13 | 244.38 | CO2 x 4 | 12 | 4 | 3 | 72.8 | 29.79 | [11 empty] | 4.91 | 1.21 | 293.26 | 586.51 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
2.13 | 244.38 | nitrogen occassionally | 10 | 4 | 2.5 | 10 | 20.04 | 20.04 | 20.79 | 1319.65 | 3519.07 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
2.27 | 48.37 | CO2 | 12 | 4 | 3 | 18.2 | 37.63 | [11 empty] | 24.81 | 5.84 | 58.04 | 116.09 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
2.27 | 48.37 | 5%CO2 / Air | 0.5 | 4 | 0.13 | 0.5 | 1.03 | [11 empty] | 1.03 | 0.26 | 1393.06 | 2786.11 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | Y
4.05 | 122.5 | CO2 x 3 | 12 | 4 | 3 | 36.4 | 29.71 | [11 empty] | 9.8 | 2.39 | 147 | 294 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
4.05 | 122.5 | 5%CO2/95%O2 | 0.17 | 4 | 0.04 | 0.17 | 0.14 | [11 empty] | 0.14 | 0.03 | 10376.47 | 20752.94 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
4.05 | 122.5 | 5%CO2/95%O2 | 3.23 | 4 | 0.81 | 3.4 | 23.73 |  |  |  |  | 23.59 | 20.86 | 2798.92 | [8 empty] | N | O2 enrichment | 23 | na | Y | Y |  | Y
4.05 | 122.5 | Nitrogen | 10 | 4 | 2.5 | 10 | 19.19 | 19.19 | 20.58 | 661.5 | 1764 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
412 | 244.38 | CO2 x 2 | 12 | 4 | 3 | 36.4 | 14.89 | [11 empty] | 4.91 | 1.21 | 293.26 | 586.51 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
4.54 | 21.6 | Nitrogen | 15 | 4 | 3.75 | 15 | 6.39 | 6.39 | 17.89 | 77.76 | 207.36 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
4.56 | 143.56 | nitrogen | 11.5 | 4 | 2.88 | 11.5 | 19.23 | 19.23 | 20.59 | 674.11 | 1797.62 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
4.43 | 122.5 | CO2 x 2 | 12 | 4 | 3 | 36.4 | 29.71 | [11 empty] | 9.8 | 2.39 | 147 | 294 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
4.52 | 374.14 | 5%H2/5%CO2/N2 | 1 | 4 | 0.25 | 1 | 0.27 | [7 empty] | 0.27 | 0.07 | 10775.23 | 21550.46 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | N | N |  | N
4.52 | 374.14 | 5%H2/5%CO2/N2 | 1 | 4 | 0.25 | 1 | 0.27 | [11 empty] | 0.13 | 0.07 | 5387.62 | 10775.23 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
4.52 | 374.14 | 5%H2/5%CO2/90%N2 | 9 | 4 | 2.25 | 9 | 20.4 | 20.45 | 20.87 | 2244.84 | 5986.24 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
6.58 | 303.9 | nitrogen x2 | 15 | 4 | 3.75 | 30 | 18.84 | 19.87 | 20.74 | 1094.04 | 2917.44 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
6.555 | 210.12 | CO2 x2 | 12 | 4 | 3 | 36.4 | 17.32 | [11 empty] | 5.71 | 1.41 | 252.14 | 504.29 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.48 | 87.89 | CO2 x 2 | 12 | 4 | 3 | 36.4 | 41.42 | [11 empty] | 13.65 | 3.3 | 105.47 | 210.94 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.01 | 171.1 | nitrogen x2 | 15 | 4 | 3.75 | 30 | 17.24 | 19.07 | 20.55 | 615.96 | 1642.56 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
6.02 | 84.2 | CO2 | 12 | 4 | 3 | 36.4 | 43.23 | [11 empty] | 14.25 | 3.44 | 101.04 | 202.08 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.04.1 | 36.1 | 5%CO2/95%O2 x 2 | 3.23 | 4 | 0.81 | 6.46 | 38.84 |  |  |  |  | 29.9 | 20.54 | 824.82 | [8 empty] | N | O2 enrichment | 23 | na | Y | Y |  | Y
6.04.1 | 36.1 | 5%CO2/95%O2 x 2 | 0.17 | 4 | 0.04 | 0.34 | 0.94 | [11 empty] | 0.47 | 0.12 | 3057.88 | 6115.76 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
6.04.1 | 36.1 | nitrogen | 15 | 4 | 3.75 | 15 | 12.22 | 12.22 | 19.02 | 129.96 | 346.56 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | Y |  | Y
6.04 | 117.8 | 5%CO2/95%O2 | 0.17 | 4 | 0.04 | 0.17 | 0.14 | [11 empty] | 0.14 | 0.04 | 9978.35 | 19956.71 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
6.04 | 117.8 | 5%CO2/95%O2 | 3.23 | 4 | 0.81 | 3.23 | 23.69 |  |  |  |  | 23.69 | 20.86 | 2691.53 | [8 empty] | N | O2 enrichment | 23 | na | Y | N |  | Y
6.05 | 88.4 | nitrogen | 15 | 4 | 3.75 | 15 | 17.35 | 17.35 | 20.15 | 318.24 | 848.64 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
6.05 | 88.4 | CO2 x4 | 12 | 4 | 3 | 72.8 | 82.35 | [11 empty] | 13.57 | 3.28 | 106.08 | 212.16 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.05 | 88.4 | LN2 | 17 | 4 | 4.25 | 17 | 16.88 | 16.88 | 20.04 | 280.8 | 748.8 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
6.06 | 206.04 | carbon dioxide | 12 | 4 | 3 | 18.2 | 8.83 | [11 empty] | 5.82 | 1.43 | 247.25 | 494.5 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.1O | 229 | carbon dioxide | 12 | 4 | 3 | 18.2 | 7.95 | [11 empty] | 5.24 | 1.29 | 274.8 | 549.6 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.73 | 94.51 | carbon dioxide | 12 | 4 | 3 | 36.4 | 38.51 | [11 empty] | 12.7 | 3.08 | 113.41 | 226.82 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.75 | 94.51 | carbon dioxide | 12 | 4 | 3 | 36.4 | 38.51 | [11 empty] | 12.7 | 3.08 | 113.41 | 226.82 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.74 | 60.47 | carbon dioxide | 12 | 4 | 3 | 36.4 | 60.2 | [11 empty] | 19.84 | 4.73 | 72.56 | 145.13 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.76 | 54.68 | nitrogen | 15 | 4 | 3.75 | 15 | 15.17 | 15.17 | 19.65 | 196.85 | 524.93 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
1.66 | 57.03 | carbon dioxide | 12 | 4 | 3 | 36.4 | 63.83 | [11 empty] | 21.04 | 5 | 68.44 | 136.87 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.62 | 58.9 | carbon dioxide | 12 | 4 | 3 | 18.2 | 30.9 | [11 empty] | 20.37 | 4.85 | 70.68 | 141.36 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.62 | 58.9 | argon | 10 | 4 | 2.5 | 10 | 17.35 | 17.35 | 20.15 | 318.06 | 848.16 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
1.34 | 123.8 | 5%CO2/95% Nitrogen | 0.1 | 4 | 0.03 | 0.1 | 0.08 | [11 empty] | 0.08 | 0.02 | 17827.2 | 35654.4 | N | STEL and LTEL | 0.5 | 1.5 | N | Y |  | N
1.34 | 123.8 | 5%CO2/95% Nitrogen | 1.9 | 4 | 0.48 | 1.9 | 20.58 | 20.58 | 20.92 | 3518.53 | 9382.74 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
1.45 | 23.19 | carbon dioxide | 3.4 | 4 | 0.85 | 3.4 | 14.66 | [11 empty] | 14.66 | 3.53 | 98.22 | 196.43 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.08 | 3.52 | carbon dioxide | 12 | 4 | 3 | 18.2 | 517.05 | [11 empty] | 340.91 | 46.01 | 4.22 | 8.45 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
1.16 | 146.5 | carbon dioxide | 12 | 4 | 3 | 36.4 | 24.85 | [11 empty] | 8.19 | 2.01 | 175.8 | 351.6 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.08 | 4.87 | carbon dioxide | 12 | 4 | 3 | 36.4 | 747.43 | [11 empty] | 246.41 | 38.12 | 5.84 | 11.69 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | gas cupboard to 6.07 | Y
6.07.1 | 55.91 | carbon dioxide | 12 | 4 | 3 | 18.2 | 32.55 | [11 empty] | 21.46 | 5.09 | 67.09 | 134.18 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.07.2 | 49.04 | carbon dioxide | 12 | 4 | 3 | 18.2 | 37.11 | [11 empty] | 24.47 | 5.76 | 58.85 | 117.7 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.07.2 | 49.04 | Nitrogen | 9.8 | 6 | 1.63 | 9.8 | 16.72 | 16.72 | 20.32 | 270.22 | 720.59 | [11 empty] | N | O2 depletion | 19.5 | 17 |  |  |  | Y
6.07.3 | 64.32 | carbon dioxide | 12 | 4 | 3 | 18.2 | 28.3 | [11 empty] | 18.66 | 4.46 | 77.18 | 154.37 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.07.4 | 50.95 | carbon dioxide | 12 | 4 | 3 | 18.2 | 35.72 | [11 empty] | 23.55 | 5.56 | 61.14 | 122.28 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.07.5 | 54.6 | carbon dioxide | 12 | 4 | 3 | 18.2 | 33.33 | [11 empty] | 21.98 | 5.21 | 65.52 | 131.04 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
6.42 | 32.87 | Nitrogen | 15 | 4 | 3.75 | 15 | 11.36 | 11.36 | 18.85 | 118.33 | 315.55 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N |  | Y
Fraser Noble
O38.1 | 277.38 | CO2 | 3.4 | 6 | 0.57 | 3.4 | 1.23 | [11 empty] | 1.23 | 0.2 | 1174.79 | 2349.57 | Y | STEL and LTEL | 0.5 | 1.5 | E | N |  | Y
O37.1 | 245.46 | hydrogen | 7.21 | 6 | 1.2 | 7.21 | 2.94 | [7 empty] | 2.94 | 0.49 | 980.48 | 1960.96 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | N |  | N
O37.1 | 245.46 | CO2 | 18.2 | 6 | 3.03 | 18.2 | 7.41 | [11 empty] | 7.41 | 1.22 | 194.21 | 388.42 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
O37.1 | 245.46 | Oxygen | 10 | 6 | 1.67 | 10 | 25.02 |  |  |  |  | 25.02 | 20.86 | 1811.49 | [8 empty] | Y | O2 enrichment | 23 | na | E | Y |  | Y
O37.1 | 245.46 | Nitrogen | 9.9 | 6 | 1.65 | 9.9 | 20.06 | 20.06 | 20.86 | 1338.87 | 3570.33 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
O33 | 193.88 | Helium | 2 | 6 | 0.33 | 2 | 20.68 | 20.68 | 20.96 | 5234.76 | 13959.36 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O23 | 822.63 | Oxygen | 15 | 6 | 2.5 | 15 | 22.77 |  |  |  |  | 22.77 | 20.94 | 4047.34 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
O23 | 822.63 | acetylene | 9.01 | 6 | 1.5 | 9.01 | 1.1 | [7 empty] | 1.1 | 0.18 | 2629.49 | 5258.99 |  |  |  |  | N | 20%LEL and 40%EL | 0.4 | 0.8 | N | N |  | Y
O23 | 822.63 | oxygen | 2 | 6 | 0.33 | 2 | 21.19 |  |  |  |  | 21.19 | 20.99 | 30355.05 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
O23 | 822.63 | acetylene | 1.7 | 6 | 0.28 | 1.7 | 0.21 | [7 empty] | 0.21 | 0.03 | 13936.32 | 27872.64 |  |  |  |  | N | 20%LEL and 40%EL | 0.4 | 0.8 | N | N |  | N
O23 | 822.63 | Argonshield light 95%Ar/5%CO2 x2 | 0.75 | 6 | 0.13 | 1.5 | 0.18 | [11 empty] | 0.09 | 0.02 | 15794.5 | 31588.99 | N | STEL and LTEL | 0.5 | 1.5 | N | N |  | N
O23 | 822.63 | Argonshield light 95%Ar/5% CO2 x2 | 14.25 | 6 | 2.38 | 28.5 | 20.18 | 20.54 | 20.94 | 3117.33 | 8312.89 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O23 | 822.63 | Argon | 15 | 6 | 2.5 | 15 | 20.52 | 20.52 | 20.94 | 2961.47 | 7897.25 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O12 | 190.01 | Helium | 15 | 6 | 2.5 | 15 | 19.25 | 19.25 | 20.73 | 684.04 | 1824.1 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O12.1 | 117.7 | CO2 | 18.2 | 6 | 3.03 | 18.2 | 15.46 | [11 empty] | 15.46 | 2.51 | 93.13 | 186.25 | Y | STEL and LTEL | 0.5 | 1.5 | E | Y | Incubators are excempt from requireing an interlock | Y
O74 | 158.65 | Nitrogen | 9.9 | 6 | 1.65 | 9.9 | 19.6 | 19.6 | 20.78 | 865.36 | 2307.64 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | H2&CH4&CO2 sensors fitted | Y
O49 | 401.97 | Hydrogen | 12 | 6 | 2 | 14.42 | 3.59 | [7 empty] | 2.99 | 0.49 | 964.73 | 1929.46 |  |  |  |  | N | 20%LEL and 40%EL | 0.8 | 1.6 | Y | N | Calculations show the risk is above the alarm levels, however, they are below the LEL for the gas. Gas detection advised | Y
O49 | 401.97 | Methane | 10 | 6 | 1.67 | 10 | 2.49 | [7 empty] | 2.49 | 0.41 | 1157.67 | 2315.35 |  |  |  |  | N | 20%LEL and 40%EL | 1 | 2 | Y | N | Calculations show the risk is above the alarm levels, however, they are below the LEL for the gas. Gas detection advised | Y
O49 | 401.97 | Nitrogen | 11.5 | 6 | 1.92 | 11.5 | 20.3 | 20.3 | 20.9 | 1887.51 | 5033.36 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O49 | 401.97 | Helium | 11.5 | 6 | 1.92 | 11.5 | 20.3 | 20.3 | 20.9 | 1887.51 | 5033.36 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
O49 | 401.97 | Carbon Dioxide | 12 | 6 | 2 | 18 | 4.48 | [11 empty] | 2.99 | 0.49 | 482.36 | 964.73 | N | STEL and LTEL | 0.5 | 1.5 | Y | N |  | Y
Liberty |  |  |  | Ind Min @4
FD06 | 146.7 | nitrogen 230bar | 3.84 | 4 | 0.96 | 3.84 | 20.35 | 20.35 | 20.86 | 2062.97 | 5501.25 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
FD06 | 146.7 | carbon dioxide | 3.4 | 4 | 0.85 | 3.4 | 2.32 | [11 empty] | 2.32 | 0.58 | 621.32 | 1242.64 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
FD06 | 147.7 | liquid nitrogen | 0.683 | 4 | 0.17 | 0.683 | 20.8 | 20.8 | 20.98 | 11677.6 | 31140.26 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
FD07 | 56.14 | carbon dioxide | 36.4 | 4 | 9.1 | 36.4 | 64.84 | [11 empty] | 64.84 | 13.95 | 22.21 | 44.42 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
Science Teaching Hub |  |  |  | Ind Min @4
2.006 | 1449 | hydrogen | 12 | 4 | 3 | 12 | 0.83 | [7 empty] | 0.83 | 0.21 | 3477.6 | 6955.2 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | N |  | Y
2.006 | 1449 | argon | 12 | 4 | 3 | 12 | 20.73 | 20.73 | 20.96 | 6520.5 | 17388 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
2.006 | 1449 | helium | 12 | 4 | 3 | 12 | 20.73 | 20.73 | 20.96 | 6520.5 | 17388 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
2.006 | 1449 | nitrogen | 12 | 4 | 3 | 12 | 20.73 | 20.73 | 20.96 | 6520.5 | 17388 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
2.001 | 1721 | nitrogen | 12 | 4 | 3 | 12 | 20.75 | 20.75 | 20.96 | 7744.5 | 20652 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | N
plant Rm | 4110 | nitrogen |  | 4 | 0 |  | 20.9 | 20.9 | 21 | #DIV/0! | #DIV/0! | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
Data Centre |  |  |  | Ind Min @4
server rm | 323 | argon/n2 fire supresent 24x80lt | 576 | 0.4 | 1440 | 576 | 16.37 | 16.37 | 3.85 | 30.28 | 80.75 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N | pressure sensor on fire suppressent no further requirements | Y
MRF
G077 PREP | 10.81 | oxygen | 0.1632 | 20 | 0.01 | 0.1632 | 22.46 |  |  |  |  | 22.46 | 20.98 | 4888.35 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
G077 | 20.76 | carbon dioxide | 3.4 | 20 | 0.17 | 3.4 | 16.38 | [11 empty] | 16.38 | 0.81 | 87.92 | 175.85 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G078 | 32.57 | carbon dioxide | 36.4 | 20 | 1.82 | 36.4 | 111.76 | [11 empty] | 111.76 | 5.29 | 12.88 | 25.77 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G065 | 32.54 | carbon dioxide | 3.4 | 20 | 0.17 | 6.8 | 20.9 | [11 empty] | 10.45 | 0.52 | 137.82 | 275.63 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G019 | 130.7 | 5000PPMCO2 N2 | 10 | 20 | 0.5 | 10 | 19.3 | 19.3 | 20.92 | 705.78 | 1882.08 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G019 | 130.7 | N2 | 10 | 20 | 0.5 | 10 | 19.3 | 19.3 | 20.92 | 705.78 | 1882.08 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G024 | 33 | oxygen | 0.18 | 20 | 0.01 | 0.18 | 21.5 |  |  |  |  | 21.5 | 20.99 | 13530 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
G027 | 45.74 | oxygen | 0.18 | 20 | 0.01 | 0.18 | 21.34 |  |  |  |  | 21.34 | 21 | 18753.4 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
G028 | 46.29 | oxygen | 0.18 | 20 | 0.01 | 0.18 | 21.34 |  |  |  |  | 21.34 | 21 | 18978.9 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
G030 | 31.52 | Oxygen | 0.18 | 20 | 0.01 | 0.18 | 21.52 |  |  |  |  | 21.52 | 20.99 | 12923.2 | [8 empty] | N | O2 enrichment | 23 | na | N | N |  | N
G032 | 56.18 | carbon dioxide | 18.2 | 20 | 0.91 | 36.4 | 64.79 | [11 empty] | 32.4 | 1.59 | 44.45 | 88.9 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G034 | 62.14 | oxygen | 4.65 | 20 | 0.23 | 4.65 | 28.43 |  |  |  |  | 28.43 | 20.92 | 986.22 | [8 empty] | N | O2 enrichment | 23 | na | Y | Y |  | Y
G034 | 62.14 | liquid nitrogen | 0.85 | 20 | 0.04 | 17 | 48.31 | 20.61 | 20.99 | 3947.72 | 10527.25 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
G038 | 44.47 | carbon dioxide | 3.4 | 20 | 0.17 | 3.4 | 7.65 | [11 empty] | 7.65 | 0.38 | 188.34 | 376.69 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G043 | 32.37 | carbon dioxide | 3.4 | 20 | 0.17 | 6.8 | 21.01 | [11 empty] | 10.5 | 0.52 | 137.1 | 274.19 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G044 | 33.09 | 1%CO2 Nitrogen | 2.83 | 20 | 0.14 | 2.83 | 19.11 | 19.11 | 20.91 | 631.4 | 1683.73 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | Y
G044 | 33.09 | carbon dioxide | 6.8 | 20 |  | 6.8 | 20.55 | [11 empty] | 20.55 | 1.02 | 70.07 | 140.15 | N | STEL and LTEL | 0.5 | 1.5 | Y | Y | Incubators are excempt from requireing an interlock | Y
G044 | 33.09 | breathing air | na | 20 | [18 empty] | N | O2 depletion | 19.5 | 17
NDC south |  |  |  | Ind Min @4
Hanger | 3622.92 | nitrogen | 15 | 4 | 3.75 | 15 |  | 20.81 | 20.98 | 13042.51 | 34780.03 | [11 empty] | N | O2 depletion | 19.5 | 17 | N | N |  | N
John Mallard PET |  |  |  | Ind Min @4
QC | 78.87 | helium | 15 | 4 | 3.75 | 15 | 16.93 | 16.93 | 20.05 | 283.93 | 757.15 | [11 empty] | N | O2 depletion | 19.5 | 17 | Y | N | druva reg out of date 21 | Y
QC | 78.87 | comp air | na | 4 |  | 10 | [16 empty] | N | O2 depletion | 19.5 | 17 |  |  | druva reg due replace 25 | Y
maintence | 52.25 | N2 5.0 | 10 | 4 | 2.5 | 10 | 16.9 | 16.9 | 20.04 | 282.15 | 752.4 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
maintence | 52.25 | N2 6.6 | 10 | 4 | 2.5 | 10 | 16.9 | 16.9 | 20.04 | 282.15 | 752.4 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
maintence | 52.25 | helium 5.5 2x1 | 20 | 4 | 5 | 20 | 12.9 | 12.9 | 19.17 | 141.08 | 376.2 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
maintence | 52.25 | N2 | 10 | 4 | 2.5 | 10 | 16.9 | 16.9 | 20.04 | 282.15 | 752.4 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
maintence | 52.25 | helium | 15 | 4 | 3.75 | 15 | 14.9 | 14.9 | 19.59 | 188.1 | 501.6 | [11 empty] | Y | O2 depletion | 19.5 | 17 | E | N |  | Y
maintence | 52.25 | hydrogen | 8.8 | 4 | 2.2 | 8.8 | 16.84 | [7 empty] | 16.84 | 4.04 | 171 | 342 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | Y |  | Y
maintence | 52.25 | hydrogen 6.0 | 8.8 | 4 | 2.2 | 8.8 | 16.84 | [7 empty] | 16.84 | 4.04 | 171 | 342 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | Y |  | Y
maintence | 52.25 | hydrogen | 2 | 4 | 0.5 | 2 | 3.83 | [7 empty] | 3.83 | 0.95 | 752.4 | 1504.8 |  |  |  |  | E | 20%LEL and 40%EL | 0.8 | 1.6 | E | N |  | Y
vault | 168.1 | Hydrogen | 2 | 4 | 0.5 | 2 | 1.19 | [7 empty] | 1.19 | 0.3 | 2420.64 | 4841.28 |  |  |  |  | Y | 20%LEL and 40%EL | 0.8 | 1.6 | E | N |  | Y

## Current Lab Gases (hidden)
Room No | Name | Volume (m³) | Approx free Air volume (m³) | Carbon Dioxide |  |  | Asphyxiant Gas - Nitrogen |  |  | Asphyxiant Gas - Helium |  |  | Oxygen
|  |  |  | No. of Bottles | Weight (Kg) | CO2 % (<0.5) | No. of Bottles | Capacity (L or m3) | O2 % (>19.5 <23.5) | No. of Bottles | Capacity (L or m3) | O2 % (>19.5 <23.5) | No. of Bottles | Capacity (L or m3) | O2 % (>19.5 <23.5)

## Common Bottle Sizes
Gas Bottle Common Sizes
| Cylinder Contents Volume | Cylinder Contents at 1 ATM |  |  |  | Cylinder Content Mass
Nitrogen |  |  | Oxygen |  | Carbon Dioxide |  | Helium
Size |  |  | Size | Volume | Size |  | Size | Volume
E33 | 8.61m³ |  | E33 | 10.07 m³ | VB | 6.35 Kg | V | 1.81 m3
E50 | 13.05 m³ |  | E50 | 15.26 m³ | VK | 34 Kg | L | 9.05 m3
G20 | 5.22 m³ |  |  |  | LB | 6.35 Kg
[5 empty] | LK | 34 Kg
X | 2.10 m³
Y | 3.84 m³
W | 9.78 m³ |  | 284915-V | 2.12 m³
Z | 12.79 m³ |  | 284913-L | 10.64 m³ | 111422-J | 25 Kg | 171698-XL | 12.98 m3
L | 50 Liters | 50 Liters
Note on C12: Tanino, Yukie: 2.10 m3
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is 50L the volume of the contents at pressure? If so, the contents at 1 atm = 50L x 200 bar/ 1atm / (1000L/m3) ~ 10m^3. Maybe move this row to column D to distinguish from other rows which I think represents contents expanded to 1 atm. Alternatively, put cylinder contents volume at atm pressure (if given).
Note on D17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is 50L the volume of the contents at pressure? If so, the contents at 1 atm = 50L x 200 bar/ 1atm / (1000L/m3) ~ 10m^3. Maybe move this row to column D to distinguish from other rows which I think represents contents expanded to 1 atm. Alternatively, put cylinder contents volume at atm pressure (if given).

## Formulas
Formulae to calculate potential oxygen depletion due to sudden release
Source: | http://www.bcga.co.uk/assets/BCGA%20GN%2011%20-%20Revision%204%20-%20For%20Publication.pdf
Formulae to calculate CO2 levels due to sudden release
Source: | http://www.bcga.co.uk/assets/BCGA%20GN%2011%20-%20Revision%204%20-%20For%20Publication.pdf
Formulae to calculate toxic gas with defined WELs levels due to slow release
Formulae to calculate inert gas (asphyxiants) levels due to slow release
Source: | https://www.parker.com/Literature/Hiross%20Zander%20Division/PDF%20Files/Bulletins/WPBREATHSAVENITRO-00-EN.pdf
Formulae to calculate Oxygen enrichment levels due to slow release
Source: | https://www.parker.com/Literature/Hiross%20Zander%20Division/PDF%20Files/Bulletins/WPBREATHSAVENITRO-00-EN.pdf
Formulae to calculate room air change rates
Note on A74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solution fails sense check: if n = 0 (no fresh air inflow), O2 concentration = 0 instead of 100%!

## Notes
https://bcga.co.uk/pubcat/codes-of-practice/
More information on HSE work place exposure limits can be found here:
https://www.hse.gov.uk/pubns/priced/eh40.pdf
Common gases and their safety limits
Gas | Limit
oxygen | Min 19.5%
Max 23.5%
Inert Gases | Use O2 minimum (19.5%)
Carbon Dioxide | Max 0.5% (1.5% if exposed for less than 15mins)
Toxic Gases | Use WELs for specific gas (can be found in SDS)
The data used in these spreadsheets was taken from guidance supplied by the British Compressed Gas Association (BCGA) Further information can be found at:
Codes of Practice - BCGA