## 5 DUNBAR STREET
| Risk Banding | Range | Inspection Frequency
NO ASBESTOS LOCATED IN RPS SURVEY OCT 2011 | High | 17+ | 1 Month or unique lock
| Significant | 15-16 | 3 Months
| Medium | 10-14 | 6 Months
| Low | 1-9 | 12 Months

## 9A DUNBAR STREET
NO FURTHER KNOWN ASBESTOS MATERIALS IN PROPERTY

## 17-19 HIGH STREET
| Risk Banding | Range | Inspection Frequency
Santia R&D survey 6/9/18 - nothing found | High | 17+ | 1 Month or unique lock
| Significant | 15-16 | 3 Months
| Medium | 10-14 | 6 Months
| Low | 1-9 | 12 Months

## 23 ST MACHAR DRIVE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1371199/0083 | 23 St Machar Drive Type 2 2009 | Basement | Plantroom | Gaskets to various pipes | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
1371199/0044 | 23 St Machar Drive Type 2 2009 | Ground | Gas meter room | Vinyl floor tiles | 4 | Chrysotile | Removed April 2026 | 3 | 1 | 4 | none
|  | Ground | Lecture Theatre | Underfloor duct adjacent entrance - pipe insulation & debris | 10 | Crocidolite | Removed April 2026 | 12 | 2 | 14 | none
|  | Ground | Kitchen 1050 | Electrical cupboard distribution board | 1 | Presumed | Needs Sampled | 6 | 4 | 10 | Manage & reinspect
1371199/0069 | 23 St Machar Drive Type 2 2009 | Ground-First | Mezzanine stairs | Nosing strips | 2 | Chrysotile | Removed April 2026 | 3 | 4 | 7 | none
1371199/0082 | 23 St Machar Drive Type 2 2009 | First | Room 51 | Floor-ceiling cement flue | 4 | Chrysotile | Removed April 2026 | 3 | 4 | 7 | none
|  | Roof space | Bindery | Cement flue remains in wall | 1 | Chrysotile | Removed April 2026 | 2 | 1 | 3 | none
Updated April 2024

## 24 HIGH STREET
Connaught carried out Type 2 survey May 2009. No Asbestos materials detected. | Risk Banding | Range | Inspection Frequency
| High | 17+ | 1 Month or unique lock
| Significant | 15-16 | 3 Months
| Medium | 10-14 | 6 Months
| Low | 1-9 | 12 Months

## 25 HIGH STREET
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1390561/0025 | 25 High Street - 2009 | Ground | Tank Cupboard | Ceiling panels | 2 | Amosite | Encapsulated by Cape 31 August 09 additional encapsulation applied 2016 | 4 | 3 | 7 | Manage & Reinspect
1390561/0025 | 25 High Street - 2009 | Ground | Tank Cupboard | Wall panels | 2 | Amosite | Encapsulated by Cape 31 August 09 additional encapsulation applied 2016 | 4 | 3 | 7 | Manage & Reinspect
|  | Ground | corridor | Firedoor | 2 | Presumed | Needs sampled | 4 | 2 | 6 | Manage & Reinspect
Updated April 2025

## 46-48 COLLEGE BOUNDS
Previous Assessments
Ground | Room G03 | Under-sink mat | 1 | Chrysotile | 1 | 1 | 0 | 1 | 3 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 6 | 2009-06-23 | Connaught/ CL | N/A | None | 2010-06-01 | Images\2009\Connaught Images\46_48 College Bounds\1390611 0020.JPG | Risk Banding | Range | Inspection Frequency
Ground | Room G03 | Under-sink mat | 1 | Chrysotile | 1 | 1 | 0 | 1 | 3 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 6 | 2011-06-15 | CL | 6 | None | 2012-06-01 | Images\2009\Connaught Images\46_48 College Bounds\1390611 0020.JPG | High | 17+ | 1 Month or unique lock
Ground | Room G03 | Under-sink mat | 1 | Chrysotile | 1 | 1 | 0 | 1 | 3 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 6 | 2012-06-25 | CL | 6 | None | 2013-06-01 | Images\2009\Connaught Images\46_48 College Bounds\1390611 0020.JPG | Significant | 15-16 | 3 Months
Ground | Room G03 | Under-sink mat | 1 | Chrysotile | 1 | 1 | 0 | 1 | 3 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 6 | 2012-06-25 | CL | 6 | None | 2013-06-01 | Images\2009\Connaught Images\46_48 College Bounds\1390611 0020.JPG | Medium | 10-14 | 6 Months
Ground | Room G03 | Under-sink mat | 1 | Chrysotile | 1 | 1 | 0 | 1 | 3 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 6 | 2013-06-19 | CL | 6 | None | 2014-06-01 | Images\2009\Connaught Images\46_48 College Bounds\1390611 0020.JPG | Low | 1-9 | 12 Months
Partial refurb carried out May/June 2019. Confirmation no asbestos in electrics and sink was replaced after 2009

## 50-52 COLLEGE BOUNDS
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1390557/0042 | 50-52 College Bounds - 2009 | Lower Ground | Plant room | Gaskets | 1 | Chrysotile |  | 3 | 2 | 5 | Manage & Reinspect
1390557/0041 | 50-52 College Bounds - 2009 | Lower Ground | Plant room | Duct mastic | 1 | Chrysotile |  | 3 | 2 | 5 | Manage & Reinspect
Updated April 2025

## 53 COLLEGE BOUNDS
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1012 | 53 College Bounds - 2015 | Basement | Boiler room | Electrical units | <1m2 | Presumed | Need sampled | 4 | 3 | 7 | Manage & Reinspect
1007 | 53 College Bounds - 2015 | Basement | Cupboard | Composite covering below vinyl | 2m2 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
1002 | 53 College Bounds - 2015 | Basement | Vestibule | Composite covering below vinyl | 12m2 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
1001 | 53 College Bounds - 2015 | Basement | Circulation | Composite covering below vinyl | 4m2 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
0001 | 53 College Bounds - 2015 | Ground | Entrance | Electrical units | <1m2 | Presumed | Need sampled | 4 | 2 | 6 | Manage & Reinspect
Updated April 2025

## 90 High Street
R&D survey carried out July 2013. Confirmation no asbestos in property

## ABERDEEN SPORTS VILLAGE
No Asbestos in this Building

## ADAM SMITH
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Adam Smith | Ground | Electrical & dry riser cupboards | Redundant fan woven textile sealant | 4 | Presumed | Needs sampled | 9 | 1 | 10 | Manage & Reinspect
| Adam Smith | First | Stairwell A | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | First | Stairwell B | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | First | Stairwell C | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | First | Stairwell D | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Second | Stairwell A | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Second | Stairwell B | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Second | Stairwell C | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Second | Stairwell D | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Third | Stairwell A | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Third | Stairwell B | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Third | Stairwell C | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Third | Stairwell D | Under window panels | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Adam Smith | Ground | Entrance Foyer | Textured coating on wall | 50 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Fyfe House March 2024 | Ground | Fire doors | Mastic / Putty | 10 | Chrysotile (presumed) | Fyfe doors were tested in March 2024 and result was positive. | 4 | 3 | 7 | Manage & Reinspect
Updated April 2025

## CULTERTY FIELD STATION
Risk Banding | Range | Inspection Frequency
High | 17+ | 1 Month or unique lock
Significant | 15-16 | 3 Months
Medium | 10-14 | 6 Months
Low | 1-9 | 12 Months
All asbestos materials removed* by Cape April 2011 after Demolition survey by Santia.
Station to be demolished 2011/12.
*Except fuseboard flashguards. Recommended to PM that Demo contractor removes.

## BALGOWNIE PAVILLION
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1248066/0019 | Balgownie 2008 | Ground | Boiler room | Pipework gaskets | 1 | Chrysotile |  | 1 | 1 | 2 | Manage & Reinspect
1248066/0019 | Balgownie 2008 | Ground | Oil store | Pipework gaskets | 1 | Chrysotile |  | 1 | 1 | 2 | Manage & Reinspect
| Balgownie 2008 | Ground | Boiler room | Electrics |  |  | Presumed by surveyor | 1 | 1 | 2 | Need sampled
#37 | Balgownie 2024 | Ground | Boiler Room | Pipe Hangers | Throughout |  | Presumed by surveyor | 1 | 1 | 2 | Need sampled
Updated April 2025

## BEDFORD ROAD
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1371222/0013 | Bedford Road Huts 2009 | M&E Main store | Room 1 electrics | Electrical cloth flash guards | 1 | Chrysotile | Needs sampled | 5 | 3 | 8 | Monitor
Updated April 2025

## BIOMEDICAL PHYSICS
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
|  | 2nd | Tank room | Gaskets ducting | 1 | Chrysotile | Encapsulated by Cape 22/11/10 | 7 | 1 | 8 | Manage & Reinspect
|  | 2nd | Tank room | Tank sealant (mastic) | 30 | Chrysotile | (Highest tank room) | 3 | 2 | 5 | Manage & Reinspect
Updated April 2025

## BOATHOUSE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1363646-0007 | Boathouse Type 2 2009 | Ground | Boatstore 1 | Electrics woven flashguards | 1 | Chrysotile | Needs sampled | 5 | 4 | 9 | Manage, remove when possible
Updated April 2025

## BURGHMUIR
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
External | Burghmuir R&D 2017 | Ground | Throughout building | Joint Mastic | All | Chrysotile | Mastic between joints is positive. | 5 | 4 | 9 | Manage & Reinspect
Updated April 2025

## BUTCHART
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Butchart | Basement | Plant room | Undercroft - pipe hangers | 1 | Chrysotile |  | 6 | 4 | 10 | Manage & Reinspect
| Butchart | Basement | Plant room | Numerous gaskets to pipework | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & Reinspect
| Butchart | Ground | 0 Office Corridor | Beam cladding | 18 | Amosite | Above 2 false ceilings. Encapsulated & labelled by Cape 3 Oct 2009 | 5 | 4 | 9 | Manage & Reinspect
| Butchart | Ground | 0 Stairs | Vertical pipe riser | 4 | Amosite | Enclosed by Rhodar Dec 08 | 5 | 4 | 9 | Manage & Reinspect
| Butchart | Ground | 0:01 Office 1 old WC Ceiling void | Beam cladding | 8 | Amosite | Encapsulated & labelled by Cape 18/03/2010 | 6 | 3 | 9 | Manage & Reinspect
| Butchart | Ground | 0:02 Office 1 Ceiling void | Beam cladding | 8 | Amosite |  | 5 | 3 | 8 | Manage & Reinspect
| Butchart | Ground | 0:03 Office 2 Ceiling void | Beam cladding | 8 | Amosite | Encapsulated & labelled by Cape 18/03/2010 | 6 | 3 | 9 | Manage & Reinspect
| Butchart | Ground | 0:05 Main hall | High level column cladding | 24 | Amosite | 8 window colums | 6 | 3 | 9 | Manage & Reinspect
| Butchart | Ground | 0:30 Reception ceiling void | Beam cladding | 10 | Amosite | Encapsulated & labelled by Cape 18/03/2010 | 6 | 3 | 9 | Manage & Reinspect
| Butchart | Ground | 0:04Electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & Reinspect
| Butchart | First - Ground | 0 Stairs | Plastic nosing strips | 20 | Chrysotile |  | 3 | 5 | 8 | Manage & Reinspect
| Butchart | First | 1 Stairs | Blue painted vertical pipe riser | 4 | Amosite | Enclosed by Rhodar Dec 08 | 5 | 4 | 9 | Manage & Reinspect
| Butchart | First | 1:03b Front Office | Beam cladding | 10 | Amosite | Loose panel removed by Cape. False ceiling sealed up. | 7 | 1 | 8 | Manage & Reinspect
| Butchart | First | 1:14 Gallery Store | Riser/column cladding | 10 | Amosite | In fair condition. Labelled | 5 | 3 | 8 | Manage & Reinspect
| Butchart | First | Main stairs ceiling void | Beam cladding | 30 | Amosite | Encapsulated & labelled by Cape 22/11/09 | 5 | 4 | 9 | Manage & Reinspect
| Butchart | First | Main stairs ceiling void | Cement Sheets | 10 | Chrysotile | Labels are recommended, but material is hard to access | 4 | 3 | 7 | Manage & Reinspect
| Butchart | External | Roof | Roof soffits | 100+ | Chrysotile | Encapsulated by Cape Sep/Oct 10 | 3 | 2 | 5 | Manage & Reinspect
Updated April 2025

## CHANONRY LODGE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
|  | Ground | Heating Chamber | Pipe insulation below and within entrance steps. | 1 | Amosite | Hole sealed by Cape Jun 2010 | 9 | 4 | 13 | Remove when possible
|  | Ground | Heating Chamber | Debris to tank | 5 | Amosite |  | 3 | 2 | 5 | Remove when possible
Updated April 2025

## CORNHILL HOSPTIAL
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
|  | Ground | Electrical cupboard | Flash guards | 1m2 | Chrysotile | Needs sampled | 5 | 1 | 6 | Manage & Reinspect
|  | Ground - 1st | Stairwell | Stair nosing strips | 8 | Chrysotile |  | 2 | 4 | 6 | Manage & Reinspect
|  | 1st | Hall 2 | Stair nosing strips | 5 | Chrysotile |  | 2 | 4 | 6 | Manage & Reinspect
|  | External, Roof | Lift motor room soffits | Presumed | 20 | Amosite | Needs sampled | 6 | 1 | 7 | Manage & Reinspect
Updated April 2025

## CROMARTY
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
|  | Ground | Building 1 kitchen | Under-sink mat | <1 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
|  | Ground | Lighthouse keepers cottage, External | Cement pipe adjacent Office 1 | 2 | Chrysotile |  | 2 | 0 | 2 | Manage & reinspect
|  | Ground | Lighthouse, external | cement drain pipe | 2 | Chrysotile |  | 2 | 0 | 2 | Manage & reinspect
|  | Ground | Lighthouse, external | Cement drain pipe | 2 | Chrysotile |  | 2 | 0 | 2 | Manage & reinspect
|  | Ground | Lighthouse, kitchen | Under-sink mat | <1 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
|  | Ground | Building kitchen | Cloth | 1 | Chrysotile | Suspected to contain asbestos | 2 | 4 | 6 | To be checked by surveyor
Updated April 2025

## CROMBIE ANNEXE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1436270-005 | Crombie Annexe TYPE2 March 2010 | Roof | Tank Room | Louvred Vents | 12 | Presumed Cement | Very Low Risk | 5 | 4 | 9 | Manage & Reinspect
Updated April 2025

## CROMBIE HALLS
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Crombie Halls Type 2 2010 | Ground | Starbucks - underfloor duct throughout | Cement shuttering to duct | 100 | Chrysotile | Discovered when floor lifted - floor resealed. | 4 | 2 | 6 | Manage & reinspect
| Crombie Halls 2024 | Ground | Duct to Johnston Halls | Electric cable cloth wrap | 30m |  | Presumed - needs tested but live | 5 | 1 | 6 | Manage & reinspect
Updated April 2025

## CRUICKSHANK
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1371187/0070 | Cruickshank TYPE2 2009 | Ground | Corridor 1 by steps | AIB Cladding to steelwork | 20 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
|  | Ground | Corridor 2, outside G. 34 | Board Cladding, above ceiling tiles | 5 | Chrysotile | Labelled | 4 | 2 | 6 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.03 | AIB Cladding to steelwork | 8 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0079 | Cruickshank TYPE2 2009 | Ground | G.05 | Gallenkamp oven lining | 1 | Chrysotile |  | 4 | 5 | 9 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.09 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.10 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.16 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.16 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.17 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0125 | Cruickshank TYPE2 2009 | Ground | G.18 | Gaskets to pipework | 1 | Chrysotile |  | 2 | 3 | 5 | Manage & reinspect
1371187/0106 | Cruickshank TYPE2 2009 | Ground | G.24 | Stair nosing strips | 15 | Chrysotile |  | 2 | 5 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.36 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.37 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.38 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.39 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.41 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0076 | Cruickshank TYPE2 2009 | Ground | G.42 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0133 | Cruickshank TYPE2 2009 | Ground | Plant Room | Gaskets to pipework | 1 | Chrysotile |  | 2 | 5 | 7 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.02 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.04 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.08 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.09 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.10 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.11 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.11 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.12 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.13 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.14 | AIB Cladding to steelwork | 5 | Chrysotile | Not encapsulated | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.20 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.21 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.22 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.23 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.25 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.26 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0042 | Cruickshank TYPE2 2009 | First | 1.27 | AIB Cladding to steelwork | 5 | Chrysotile | Encapsulated by Cape Sep 09 | 5 | 5 | 10 | Manage & reinspect
1371187/0039 | Cruickshank TYPE2 2009 | First | Corridor by Firedoor | AIB Cladding to steelwork | 20 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
|  | Second | Corridor 2 | AIB Cladding to steelwork | 20 | Chrysotile | Presumed behind partition wall | 4 | 3 | 7 | Manage & reinspect
|  | Second | Corridor 1 | AIB Cladding to steelwork | 20 | Chrysotile | Presumed behind partition wall | 4 | 3 | 7 | Manage & reinspect
|  | Second | 2.06 | AIB Cladding to steelwork concealed behind fume cabinet | 2 | Chrysotile | Encapsulated by Cape Sep 11 | 4 | 3 | 7 | Manage & reinspect
1371187/0014 | Cruickshank TYPE2 2009 | Roof | Loft over 2.02 | AIB Cladding to steelwork | 2 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
1371187/0014 | Cruickshank TYPE2 2009 | Roof | Loft over 2.05 | AIB Cladding to steelwork | 2 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 3 | 7 | Manage & reinspect
Note: AIB beam cladding rises behind corridor walls full height of building
Updated April 2025

## CRUICKSHANK BOTANICS BOTHY
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Botanics MS 2017.pdf | Ground | Throughout | All electrical switchgear throughout | 2 |  | Needs sampled | 4 | 4 | 8 | Manage & reinspect
| Botanics MS 2017.pdf | Ground | Plantroom | Gaskets to pipework regulator | 2 |  |  | 4 | 2 | 6 | Manage & reinspect
Updated April 2025

## EDWARD WRIGHT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1248048-0013 | Edward Wright Type 2 2008.pdf | Basement | Duct | Pipe brackets - board packing | 1 | Amosite | Inaccessible unless pipes removed | 7 | 3 | 10 | Manage & reinspect
1248048-0012 | Edward Wright Type 2 2008.pdf | Basement | Duct | Rope to pipe hangers | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0011 | Edward Wright Type 2 2008.pdf | Basement | Duct | Pipework gaskets | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0277 | Edward Wright Type 2 2008.pdf | Lower ground | A block landing electric cupboard | Flashguards | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0131 | Edward Wright Type 2 2008.pdf | Ground | G76 | Fire door core | 2 | Amosite | Similar to all kitchen doors - needs sampled | 5 | 4 | 9 | Material is fully enclosed
1248048-0026 | Edward Wright Type 2 2008.pdf | Ground | G96a | Rope seal to safe. | 1 | Chrysotile |  | 5 | 4 | 9 | Manage & reinspect
|  | Ground | Plantroom | Pipework gaskets | 1 | Chrysotile |  | 5 | 4 | 9 | Manage & reinspect
1248048-0079 | Edward Wright Type 2 2008.pdf | Ground | G77 riser | Panel to bottom right hand wall | 2 | Amosite | Shuttering panel in base of riser | 7 | 1 | 8 | Manage & reinspect
1248048-0259 | Edward Wright Type 2 2008.pdf | Ground | B Block LHS corridor electric cupboard | Flashguards | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0259 | Edward Wright Type 2 2008.pdf | Ground | B Block RHS corridor electric cupboard | Flashguards | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0259 | Edward Wright Type 2 2008.pdf | Ground | A block landing electric cupboard | Flashguards | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0259 | Edward Wright Type 2 2008.pdf | Ground | C block landing electric cupboard | Flashguards | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
|  | Ground | Data Centre | Cement shuttering to underside of ring beam | 50 | Chrysotile | Built into wall. Section exposed to allow installation of louvres, encapsulated by Cape April 13 | 3 | 1 | 4 | Inspection not possible, built into wall. NB May exist elsewhere in construction of Edward Wright.
1248048-0131 | Edward Wright Type 2 2008.pdf | First | F76 | Fire door core | 2 | Amosite | Similar to all kitchen doors - needs sampled | 5 | 4 | 9 | Material is fully enclosed
1248048-0323 | Edward Wright Type 2 2008.pdf | First | Electrics riser 5 | Ceiling | 2 | Amosite | Encapsulated by Cape 5/12/09 | 4 | 4 | 8 | Manage & reinspect
1248048-0184 | Edward Wright Type 2 2008.pdf | First | F77 riser | Pipe bracket packer | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0047 | Edward Wright Type 2 2008.pdf | First | Roofspace 1 | Roof felt | 1 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
1248048-0259 | Edward Wright Type 2 2008.pdf | First | A block landing electric cupboard | Flashguards | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0131 | Edward Wright Type 2 2008.pdf | Second | S76 | Fire door core | 2 | Amosite | Similar to all kitchen doors - needs sampled | 5 | 4 | 9 | Material is fully enclosed
1248048-0187 | Edward Wright Type 2 2008.pdf | Second | S77 riser | Pipe bracket packer | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0277 | Edward Wright Type 2 2008.pdf | Second | A block landing electric cupboard | Flashguards | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
1248048-0188 | Edward Wright Type 2 2008.pdf | Second | S77 riser | Cement packers to top of brickwork | 1 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
Updated April 2025

## ELPH ROAD STORES
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Elph Rd Stores MS 2017 | Ground | Main Stores Building | Live electrical switchgear | 1 m |  | Needs sampled | 4 | 1 | 5 | Manage & reinspect
| Elph Rd Stores MS 2017 | Roof | Main Stores Building | Cement Panels to low level roof | 50 m2 | Cement |  | 4 | 1 | 5 | Manage & reinspect
| Elph Rd Stores MS 2017 | Roof | Main Stores Building | Cement Panels to high level roof north side | 75 m2 | Cement |  | 4 | 1 | 5 | Manage & reinspect
| Elph Rd Stores MS 2017 | Roof | Main Stores Building | Cement Panels to high level gable end | 20 m2 | Cement |  | 4 | 1 | 5 | Manage & reinspect
Updated April 2025

## FRASER NOBLE COURT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
NC1157 | Sureclean survey 2007 | Under Ground Floor | Damp Proof Course | Damp Proof Course |  | Chrysotile | Very low potential to release fibres | 1 | 1 | 2 | NHS Highland responsibility
NC1158 | Sureclean survey 2008 | Calorifier room | Tank Top Gasket | Tank Top Gasket |  | Chrysotile | Very low potential to release fibres | 1 | 1 | 2 | NHS Highland responsibility
This building is maintained by NHS. Information is here for general awareness only
Updated April 2025

## FRASER NOBLE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Fraser Noble | Basement | -1/001 Plant room | Gaskets to ventilation ducting | 50 | Chrysotile |  | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | Basement | -1/002 Pump Booster | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 5 | 10 | Manage & reinspect
| Fraser Noble | Basement | -1/003 Plenum Chamber | Corrugated panelling/shuttering | 4 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fraser Noble | Ground | West block south stair west riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | West block south stair west riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | West block south stair east riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | West block south stair east riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | West block North stair west riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | West block North stair west riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | West block North stair west riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | West block North stair west riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | East block Room 071 north riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | East block Room 071 north riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | East block Room 071 south riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | East block Room 071 south riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | East block Room 070 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | East block Room 070 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | East block Room 068 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | Ground | East block Room 068 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | Ground | NW Stair riser cupboard | Bitumastic material around pipe insulation | 10 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | Ground | SW stair riser Cupboard | Bitumastic material around pipe insulation | 10 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | Ground | Room 012 | Bitumastic material around pipe insulation | 10 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | Ground | 63 | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 63 | Pipe hanger brackets | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 64 | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 65 | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 66 | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 71 | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 71 | Pipe hanger brackets | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 006 Store | Sprayed coating to ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 2 | 8 | Manage & reinspect
| Fraser Noble | Ground | 007 Switch Room | Sprayed coating to ceiling | 15 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 008 Computer Room | Sprayed coating to ceiling | 30 | Amosite | Encapsulation carried out by Rhodar Dec 09 | 6 | 4 | 10 | Manage & reinspect
| Fraser Noble | Ground | 008 Computer Room | Gaskets to ventilation ducting | 1 | Chrysotile |  | 4 | 6 | 10 | Manage & reinspect
| Fraser Noble | Ground | 009 Computer Room | Sprayed coating to ceiling | 10 | Amosite | Encapsulation carried out by Rhodar Dec 09 | 6 | 4 | 10 | Manage & reinspect
| Fraser Noble | Ground | 009 Computer Room | Gaskets to ventilation ducting | 1 | Chrysotile |  | 4 | 6 | 10 | Manage & reinspect
| Fraser Noble | Ground | 011 | Sprayed coating to ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 4 | 10 | Manage & reinspect
| Fraser Noble | Ground | 012 | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 6 | 11 | Manage & reinspect
| Fraser Noble | Ground | 013 Laboratory | Encapsulated remains of sprayed coating to ceiling | 150 | Amosite | Encapsulation completed by Rhodar 20/1/10 | 6 | 6 | 12 | Manage & reinspect
| Fraser Noble | Ground | 013 Laboratory | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 6 | 11 | Manage & reinspect
| Fraser Noble | Ground | 014 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 015 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 017 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 018 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 019 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 020 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 023 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 024 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 025 | Sprayed coating above false ceiling | 40 | Amosite | Encapsulated with double-skin boarded ceiling. | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | Ground | 047 | Pipe hanger brackets | 1 | Chrysotile | Presumed | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | Ground | Throughout area around original columns | Asbestos sheest used as form work | 1m zone around each column |  | Strongly presumed | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | Ground | 061 Laser Lab | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | 062 Laser Lab | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | East Corridor | Pipe hanger brackets | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | East Corridor | Air handling duct joint seal | 1 | Chrysotile | Throughout area. | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | Ground | South Corridor | Gaskets to ventilation ducting | 1 | Chrysotile |  | 4 | 2 | 6 | Manage & reinspect
| Fraser Noble | 1 | West block south stair west riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | West block south stair west riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | West block south stair east riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | West block south stair east riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | West block north stair west riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | West block north stair west riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | West block north stair east riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | West block north stair east riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | West block corridor north riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | West block corridor north riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | West block corridor south riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | West block corridor south riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | East block room 171 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | East block room 171 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | East block room 172 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | East block room 172 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | East block room 174 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | East block room 174 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | East block room 176 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 1 | East block room 176 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 1 | Room 101 Main lecture theatre | Debris behind ventilation grilles,both sides (Material is not in airflow-is in void behind ducting) | 2 | Amosite | Is presumed to be throughout LT, behind timber cladding and is debris from contaminated roof void above. Inspection of timber facings only | 11 | 4 | 15 | Planning has begun on full decontamination of LT & void
| Fraser Noble | 1 | Room 102 Female WC | Toilet Cistern | 1 | Chrysotile |  | 2 | 4 | 6
| Fraser Noble | 1 | Room 108 Male WC | Toilet Cistern | 1 | Chrysotile |  | 2 | 4 | 6
| Fraser Noble | 1 | Room 110 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Enclosed
| Fraser Noble | 1 | Room 111 (was 113 & 116) | Noggins embedded in concrete window sill | 2 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Enclosed
| Fraser Noble | 1 | Room 112 (was 117 & 118) | Noggins embedded in concrete window sill | 2 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Enclosed
| Fraser Noble | 1 | Room 113 (was 119 & 120) | Noggins embedded in concrete window sill | 2 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Enclosed
| Fraser Noble | 1 | Room 114 (was 122, 123 & 124) | Noggins embedded in concrete window sill | 2 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Enclosed
| Fraser Noble | 1 | Room 115 (was 125) | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Enclosed
| Fraser Noble | 1 | Room 116 (was 129) | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Enclosed
| Fraser Noble | 1 | Room 171 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 172 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 172 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 1 | Room 173 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 173 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 1 | Room 174 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 175 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 176 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 176 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 1 | Room 179 toilet | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 4 | 10 | Manage & reinspect
| Fraser Noble | 1 | Room 180 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 180 | Panel in riser to rear of corridor radiator | 2 | Chrysotile |  | 6 | 4 | 10 | Manage & reinspect
| Fraser Noble | 1 | Room 181 | Panels in radiator enclosures | 15 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 186 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 187 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 188 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 189 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 190 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 191 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 192 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 193 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 194 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 195 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 197 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | Room 199 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 1 | NW Stair riser cupboard | Bitumastic material around pipe insulation | 10 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | 1 | SW stair riser Cupboard | Bitumastic material around pipe insulation | 10 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | 1 | West service Cupboards | Bitumastic material around pipe insulation | 10 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | 2 | West block corridor south riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | West block corridor south riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | East block room 250 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | East block room 250 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | East block room 252 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | East block room 252 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | East block room 254 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | East block room 254 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | East block room 255 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | East block room 255 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | East block room 259 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | East block room 259 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | East block room 281 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | East block room 281 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | East block room 282 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 2 | East block room 282 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 2 | Dome over LT1 | Widespread sprayed asbestos debris | 100 | Amosite | Area locked, no access allowed. Full decn required. | 11 | 4 | 15 | Full decon. Area closed
| Fraser Noble | 2 | Electrical cupboard 285 | Panel behind radiator in void | 2 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fraser Noble | 2 | Room 201 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 201 | Bitumastic material around pipe insulation | 20 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | 2 | Room 206 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 207 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 208 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 210 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 211 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 215 | Bitumastic material around pipe insulation | 5 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | 2 | Room 212 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 213 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 214 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 215 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 216 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 219 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 205 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 228 | Noggins embedded in concrete window sill | 1 | Amosite | Encapsulated by Rhodar June 2011. Concealed behind new cladding | 4 | 5 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 250 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 251 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 252 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 252 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 253 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 253 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 254 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 255 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 255 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 256 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 256 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 2 | Room 258 toilet | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 4 | 10 | Manage & reinspect
| Fraser Noble | 2 | Room 259 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 260 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 261 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 262 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 263 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 264 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 265 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 266 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 267 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 268 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 269 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 270 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 271 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 272 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 273 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 274 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 275 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 276 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 277 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 278 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 279 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 280 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 281 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 282 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 283 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 2 | Room 258 WC | Toilet cistern | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Fraser Noble | 3 | East block room 350 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 3 | East block room 350 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 3 | East block room 352 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 3 | East block room 352 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 3 | East block room 353 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 3 | East block room 353 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 3 | East block room 355 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 3 | East block room 355 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 3 | East block room 360 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 3 | East block room 360 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 3 | East block room 382 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 3 | East block room 382 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 3 | East block room 383 riser | Pipe hanger brackets | 1 | Chrysotile |  | 5 | 1 | 6 | Manage & reinspect
| Fraser Noble | 3 | East block room 383 riser | Bitumen coating on cork insulated pipework | 10 | Chrysotile |  | 3 | 1 | 4 | Manage & reinspect
| Fraser Noble | 3 | Room 306 | AHU ducting joint sealant | 1 | Chrysotile | Labelled & encapsulated | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 306 | Pipe hanger brackets | 1 | Chrysotile | Labelled & encapsulated | 4 | 4 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 350 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 351 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 352 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 352 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 3 | Room 353 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 354 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 355 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 355 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 3 | Room 356 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 358 toilet | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 4 | 10 | Manage & reinspect
| Fraser Noble | 3 | Room 360 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 361 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 362 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 363 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 364 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 365 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 366 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 367 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 368 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 369 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 370 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 371 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 372 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 373 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 374 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 375 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 376 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 377 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 378 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 379 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 380 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 381 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 382 | Panels in radiator enclosures | 5 | Chrysotile |  | 6 | 5 | 11 | Manage & reinspect
| Fraser Noble | 3 | Room 383 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 3 | Room 383 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
| Fraser Noble | 3 | Room 384 | Panel in riser to rear of corridor radiator | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Fraser Noble | 3 | Room 384 | Panels in radiator enclosures | 5 | Chrysotile | Encapsulated by Cape | 3 | 5 | 8 | Manage & reinspect
Updated April 2025

## FYFE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Fyfe House | Ground | Electrical & dry riser cupboards | Redundant fan woven textile sealant | 4 | Presumed | Needs sampled | 9 | 1 | 10 | Manage & reinspect
| Fyfe House | First | Stairwell A | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | First | Stairwell B | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | First | Stairwell C | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | First | Stairwell D | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Second | Stairwell A | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Second | Stairwell B | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Second | Stairwell C | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Second | Stairwell D | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Third | Stairwell A | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Third | Stairwell B | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Third | Stairwell C | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Third | Stairwell D | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Fyfe House | Ground | Entrance Foyer | Textured coating on wall | 50 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
| Fyfe House Sept 2019 | Ground | Fire doors | Mastic / Putty | 10 | Chrysotile |  | 4 | 3 | 7 | Manage & Reinspect
Updated April 2025

## GRANT COURT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Burnett House | Ground | Block 12 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | Ground | Block 13 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | Ground | Block 14 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | Ground | Block 15 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Grant Court | Ground | Block 16 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | Ground | Block 17 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | Ground | Block 18 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | Ground | Block 19 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Burnett House | 1st | Block 12 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | 1st | Block 13 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | 1st | Block 14 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | 1st | Block 15 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Grant Court | 1st | Block 16 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | 1st | Block 17 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | 1st | Block 18 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | 1st | Block 19 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Burnett House | 2nd | Block 12 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | 2nd | Block 13 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | 2nd | Block 14 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Burnett House | 2nd | Block 15 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & Reinspect
| Grant Court | 2nd | Block 16 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | 2nd | Block 17 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | 2nd | Block 18 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | 2nd | Block 19 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | 4 | 1 | 5 | Manage & reinspect
| Grant Court | 2nd | Block 16 Roofspace | Damp proof membrane | 8 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Grant Court | 2nd | Block 17 Roofspace | Damp proof membrane | 8 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Grant Court | 2nd | Block 18 Roofspace | Damp proof membrane | 8 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Grant Court | 2nd | Block 19 Roofspace | Damp proof membrane | 8 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Grant Court | Plant Room | Floor | Adhesive | 1 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Grant Court | Plant Room | Floor within cupboard | Floor tiles | 1 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Burnett House | Roof | Block 12 | Tank room damp membrane | 100 | Chrysotile |  | 3 | 5 | 8 | Manage & Reinspect
| Burnett House | Roof | Block 13 | Tank room damp membrane | 100 | Chrysotile |  | 3 | 5 | 8 | Manage & Reinspect
| Burnett House | Roof | Block 14 | Tank room damp membrane | 100 | Chrysotile |  | 3 | 5 | 8 | Manage & Reinspect
| Burnett House | Roof | Block 15 | Tank room damp membrane | 100 | Chrysotile |  | 3 | 5 | 8 | Manage & Reinspect
Previous Assessments
|  | Ground | Block 16 Plantroom | Flange joints | 1 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 17 Kitchen 1 | Beige & brown Floor tiles | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 17 WC2 | Brown floor tiles | 4 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 17 Plantroom | Gasket to spare pump | 1 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Laundry | Brown floor tiles | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 17 Kitchen 2 | Brown floor tiles | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 17 Plantroom | Flange joints | 1 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 18 Plantroom | Flange joints | 1 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 19 Plantroom | Flange joints | 1 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 16 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 17 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 18 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 16 Plantroom | Flange joints | 1 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | Ground | Block 17 Kitchen 1 | Beige & brown Floor tiles | 8 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | Ground | Block 17 WC2 | Brown floor tiles | 4 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | Ground | Block 17 Plantroom | Gasket to spare pump | 1 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Laundry | Brown floor tiles | 8 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | Ground | Block 17 Kitchen 2 | Brown floor tiles | 8 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | Ground | Block 17 Plantroom | Flange joints | 1 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | Ground | Block 18 Plantroom | Flange joints | 1 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | Ground | Block 19 Plantroom | Flange joints | 1 | Chrysotile | Removed by Cape during refurb Summer 2013 | #REF! | #REF! | #REF!
|  | 2nd | Block 16 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 17 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 18 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 16 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 17 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 18 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 16 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 16 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 16 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | Ground | Block 17 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 17 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 17 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | Ground | Block 18 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 18 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 18 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | Ground | Block 19 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 19 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 16 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 17 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 18 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Roofspace | Damp proof membrane | 8 | Chrysotile |  | #REF! | #REF! | #REF!
|  | Ground | Block 16 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 16 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 16 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | Ground | Block 17 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 17 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 17 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | Ground | Block 18 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 18 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 18 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | Ground | Block 19 plantroom | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 1st | Block 19 Drying Room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
|  | 2nd | Block 19 Store room | Wadding in electrical conduit | 0.5 | Chrysotile | Conduit has been sealed shut | #REF! | #REF! | #REF!
Updated April 2025

## HEALTH SCIENCES BUILDING
NO ASBESTOS IN THIS BUILDING

## HECTOR BOECE COURT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
|  | External | Block 20 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 21 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 22 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 23 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 24 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 25 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 26 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 27 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 28 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 29 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
|  | External | Block 30 | Roof soffit | 30 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
Updated April 2025

## HILLHEAD SEWAGE LIGHT STORE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
AP001785-0319/0001 | Hillhead Light Store | Ground | Light Store | Fuse Linings | 6 | Chrysotile | Needs sampled | 2 | 4 | 6 | Manage & reinspect
AP001785-0319/0004 | Hillhead Light Store | Ground | Sewage Room | Fuse Linings | 8 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
AP001785-0319/0012 | Hillhead Light Store | Ground | Light & Sewage Room | Mastic | 12m | Chrysotile |  | 2 | 3 | 5 | Manage & reinspect
Updated April 2025

## HILLHEAD CENTRAL
No asbestos in this building

## HILLHEAD LAUNDRIES
| Risk Banding | Range | Inspection Frequency
Santia survey carried out December 2010 - No asbestos materials found. | High | 17+ | 1 Month or unique lock
| Significant | 15-16 | 3 Months
| Medium | 10-14 | 6 Months
| Low | 1-9 | 12 Months

## HUMANITY MANSE
No asbestos in this building

## IMS
No asbestos in this building

## HILLHEAD MAIN BOILER
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Hillhead Main Boiler | Ground | Rest Room fuseboard | Flash guards | 1 | Chrysotile | Needs sampled | 3 | 4 | 7 | Manage & reinspect
| Hillhead Main Boiler | Ground | Windows | Rope seals | 20 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
Updated April 2025

## HILLHEAD SPORTS CENTRE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Hillhead Sports Centre | Ground | Physio 1 | Adhesive below flooring | 10 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | Ground | Physio 2 | Adhesive below flooring | 10 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | Ground | Treatment Room | Adhesive below flooring | 8 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | Ground | Staff Room | Adhesive below flooring | 5 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | Ground | Disabled WC | Adhesive below flooring | 2 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | Ground | Vestibule | Adhesive below flooring | 4 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | Ground | Main Stairs | Adhesive below flooring | 10 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | First | Kitchen | Adhesive below flooring | 5 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Hillhead Sports Centre | External | Out building 1 | Corrugated roof & walls | 80 | Chrysotile | ACM is generally degrading, but is not immediately hazardous. | 4 | 4 | 8 | Manage & reinspect
| Hillhead Sports Centre | External | Out building 1 | Bitumen material to sheeting | 10 | Chrysotile |  | 4 | 4 | 8 | Manage & reinspect
| Hillhead Sports Centre | External | Out building 1 | Infill panel over door | 2 | Chrysotile |  | 4 | 4 | 8 | Manage & reinspect
Updated April 2025

## HILLHEAD WATER PUMP HOUSE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Hillhead Water Pump House | Ground | Generator Room | Insulation/packing to sleeve through rear wall | 1 | Amosite | Encapsulated and labelled by Cape nov 16 | 5 | 3 | 8 | Manage & reinspect
| Hillhead Water Pump House | Ground | Pump Room | Ceiling Panels | 25 | Amosite | Encapsulated & labelled by Pyeroy Dec 10 | 4 | 3 | 7 | Manage & reinspect
| Hillhead Water Pump House | Ground | Generator Room | Ceiling Panels | 20 | Amosite | Encapsulated & labelled by Pyeroy Dec 10 | 4 | 3 | 7 | Manage & reinspect
| Hillhead Water Pump House | Ground | Generator Room | Cement sleeve through rear wall | 2X1 | Chrysotile | Encapsulated and labelled by Cape nov 16 | 2 | 3 | 5 | Manage & reinspect
| Hillhead Water Pump House | Ground | External | Roof Undercloak | 20 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
Updated April 2025

## HILLHEAD OLD SHOP
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1519892-0006 | Hillhead Shop Survey - 2011 | Ground | Shop G01 | Within Ceiling Void - Corrugated Roof Sheeting | 85m2 | Chrysotile | Reverse of external sheeting | 4 | 5 | 9 | Manage & reinspect
1519892-0010 | Hillhead Shop Survey - 2011 | Ground | Toilet G02 | Corrugated Roof Sheeting | 8m2 | Chrysotile |  | 4 | 4 | 8 | Manage & reinspect
1519892-0004 | Hillhead Shop Survey - 2011 | Ground | Store G04 | Corrugated Roof Sheeting | 20m2 | Chrysotile | Reverse of external sheeting | 4 | 5 | 9 | Manage & reinspect
| Hillhead Shop Survey - 2011 | Ground | Bar Store G07 | Corrugated Roof Sheeting | 25m2 | Chrysotile | Reverse of external sheeting | 4 | 5 | 9 | Manage & reinspect
1519892-0001 | Hillhead Shop Survey - 2011 | Ground | Store G08 | Corrugated Roof Sheeting | 25m2 | Chrysotile | Reverse of external sheeting | 4 | 5 | 9 | Manage & reinspect
1519892-0015 | Hillhead Shop Survey - 2011 | Ground | Switch Room G09 | Profile Cement Roofing | 15m2 | Chrysotile | Reverse of external sheeting | 4 | 5 | 9 | Manage & reinspect
1519892-0011 | Hillhead Shop Survey - 2011 | Ground | Store G10 | Corrugated Roof Sheeting | 25m2 | Chrysotile | Reverse of external sheeting | 4 | 5 | 9 | Manage & reinspect
1519892-0017 | Hillhead Shop Survey - 2011 | Ground | External Roof | Corrugated Roof Sheeting | 100m2 | Chrysotile | Encapsulated by Cape externally 2009 | 4 | 3 | 7 | Manage & reinspect
AP001785-03-29/0020 | Hillhead Shop 2019 | Ground | Store room | Gaskets to gas meter | 3 items | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
AP001785-03-29/0027 | Hillhead Shop 2019 | Ground | Plant Room | Gaskets to the flanges of the unlagged pipework on the back and right hand wall | 8 items | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
1519892-0015 | Hillhead Shop Survey - 2011 | Ground | Switch Room G09 | Electric Flash Guards | 1 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
Updated April 2025

## HUB
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
AP001785-03-14/0095 | 2022 | Ground | Office Area 020 / 020a Ceiling Void | Insulating Board Residue to Stramit Board | 50m2 | Amosite | Unsealed Board | 9 | 5 | 14 | Manage & Inspect
AP001785-03-14/0115 | 2022 | Ground | Plant Room 041 Walls / External Door | Bitumen Dpc | 10m run | Amosite | Reinforced - Composite Materials | 4 | 6 | 10 | Manage & Inspect
AP001785-03-14/0129 | 2022 | Ground | Main Reception Disabled Toilet Ceiling Void | Insulating Board Debris | 10m2 | Amosite | Unsealed Board | 9 | 5 | 14 | Manage & Inspect
AP001785-03-14/0140 | 2022 | Ground | Female Toilet Cloakroom Ceiling Void | Insulating Board Residue Small Amounts | Residue | Amosite | Unsealed Board | 9 | 1 | 10 | Manage & Inspect
AP001785-03-14/0141 | 2022 | Ground | Female Toilet Cloakroom Void Ceiling | Insulating board residue Small Amounts | Residue | Amosite | Unsealed Board | 9 | 1 | 10 | Manage & Inspect
AP001785-03-14/0143 | 2022 | Ground | Female Toilet Cloakroom Void Floor | Insulating Board debris Small Amounts | Residue | Amosite | Debris | 10 | 3 | 13 | Manage & Inspect
SAM10005077/0184 | 2022 | Ground | Male Toilet Roof Void Ceiling void | Debris Throughout | Residue | Amosite | Debris | 10 | 4 | 14 | Manage & Inspect
SAM10005077/0185 | 2022 | Ground | Foyer Ceiling Void Ceiling void floor | Debris Throughout | Residue | Amosite | Debris | 10 | 4 | 14 | Manage & Inspect
AP001785-03-14/0113 | 2022 | Ground | Plant Room 041 Walls | Residue Throughout | Residue | Asbestos | Enclosed Spray/Lagging | 10 | 5 | 15 | Manage & Inspect
AP001785-03-14/0128 | 2022 | Ground | Main Reception Disabled Toilet Ceiling Void | Insulating Board Residue Small Amounts | Residue | Asbestos | Unsealed Board | 10 | 5 | 15 | Manage & Inspect
AP001785-03-14/0133 | 2022 | Ground | Male Toilet Cloakroom Ceiling Void | Insulating Board Residue Small Amounts | Residue | Asbestos | Unsealed Board | 10 | 3 | 13 | Manage & Inspect
AP001785-03-14/0161 | 2022 | Ground | Foyer Stramit board | Insulating board residue | 20m2 | Asbestos | Debris | 8 | 2 | 10 | Manage & Inspect
AP001785-03-14/0163 | 2022 | Ground | Recording studio 011 Stramit board | Insulating board residue | 12m2 | Asbestos | Debris | 8 | 2 | 10 | Manage & Inspect
AP001785-03-14/0165 | 2022 | Ground | Electrical cupboard 2 Stramit board | Insulating board residue | 9m2 | Asbestos | Debris | 8 | 2 | 10 | Manage & Inspect
AP001785-03-14/0168 | 2022 | Ground | Office 1 Ceiling Void | Residue Small Amounts | Residue | Asbestos | Unsealed Board | 10 | 6 | 16 | Manage & Inspect
AP001785-03-14/0179 | 2022 | Ground | Office 2 Ceiling Void | Residue Small Amounts | Residue | Asbestos | Unsealed Board | 7 | 6 | 13 | Manage & Inspect
AP001785-03-14/0180 | 2022 | Ground | Office 3 Ceiling Void | Residue Small Amounts | Residue | Asbestos | Unsealed Board | 7 | 6 | 13 | Manage & Inspect
| 2022 | Ground | Main Plant room | Debris to walls - inaccessible for full cleaning, on the 2 walls adj. DHW vessel | 1 | Amosite | Area cleaned AFAP by Cape Oct 16 | 5 | 2 | 7 | Remediate as far as possible, encapsulate walls
| 2022 | Ground | Management Suite | Debris in ceiling void | 1 | Amosite |  | 5 | 3 | 8 | Access to ceiling void restricted
| 2022 | Ground | Reception foyer | Debris in ceiling void | 2 | Amosite |  | 6 | 1 | 7 | Access to ceiling void restricted
| 2022 | Ground | Electrical cupboard, | Debris in ceiling void | 2 | Amosite |  | 4 | 2 | 6 | Access to ceiling void restricted
| 2022 | Ground | Room 011 | Debris in ceiling void | 2 | Amosite |  | 5 | 1 | 6 | Access to ceiling void restricted
| 2022 | Ground | Sink area adj room 11 | Debris in ceiling void | 2 | Amosite |  | 2 | 4 | 6 | Access to ceiling void restricted
| 2022 | Ground | Male & Female WCs | Debris in ceiling void | 2 | Amosite |  | 1 | 3 | 4 | Access to ceiling void restricted
| 2022 | Ground | Mezz service void | Debris on floor | 2 | Amosite | Area cleaned AFAP by Cape Oct 16 | 5 | 5 | 10 | Access to ceiling void restricted
| 2022 | Ground | Room 023 | Debris in ceiling void above strammit board. Encapsulated and labelled | 1 | Amosite |  | 8 | 2 | 10 | Plywood over hole in strammit board. Hole goes through to sprayed coating. Board cant be removed.
| 2022 | Ground | Room 022 | Debris in ceiling void above strammit board. Encapsulated and labelled | 1 | Amosite |  | 10 | 3 | 13 | Plywood over hole in strammit board. Hole goes through to sprayed coating. Board can't be removed.
| 2022 | Ground | Room 023 | AIB under window sills | 1 | not sampled, but 99.9% certain | found 16/07/18 by Dmal | 5 | 4 | 9 | Possible to be the same for all windows throughout building
AP001785-03-14/0081 | 2022 | 1 | Disabled Toilet 120 Block Wall (Ceiling Void) | Insulating Board Residue Small Amounts | Residue | Amosite | Unsealed Board | 9 | 5 | 14 | Manage & Inspect
| 2022 | 1 | Disabled WC | Debris on wall in ceiling void | 1 | Amosite |  | 5 | 2 | 7 | Access to ceiling void restricted
AP001785-03-14/0084 | 2022 | 1 | Male Toilet 122 Walls Within Cavity / Ceiling Void | Textured Coating | 18m2 | Amosite | Painted/Encapsulated Board | 6 | 5 | 11 | Manage & Inspect
AP001785-03-14/0028 | 2022 | 2 | Roof Access 1 Stairs | Stair Nosing | 2m run | Chrysotile | Reinforced - Composite Materials | 3 | 3 | 6 | Manage & Inspect
AP001785-03-14/0042 | 2022 | 2 | Electrical Cupboard 1 Joists | Insulating Board Small Amounts | Residue | Amosite | Unsealed Board | 9 | 3 | 12 | Manage & Inspect
| 2022 | 2 | Lift motor room | Debris on ledges | 2 | Amosite |  | 3 | 3 | 6 | Environmental clean
| 2022 | 2 | Main stair foyer | Debris in ceiling void | 1 | Amosite |  | 3 | 4 | 7 | Access to ceiling void restricted
| 2022 | 2 | Water tank room | Encapsulated debris to strawboard walls | 2 | Amosite |  | 3 | 4 | 7 | Monitor
AP001785-03-14/0001 | 2022 | 3 | Water Tank Room Walls | Residue Small Amounts | Residue | Amosite | Painted/Encapsulated Board | 8 | 6 | 14 | Manage & Inspect
AP001785-03-14/0004 | 2022 | 3 | Water Tank Room Ledge at Top of Wall | Insulating Board Debris | 8m run | Amosite | Debris | 10 | 3 | 13 | Manage & Inspect
AP001785-03-14/0007 | 2022 | 3 | Access Corridor Stramit Board | Residue Small Amounts | Residue | Asbestos | Painted/Encapsulated Board | 9 | 2 | 11 | Manage & Inspect
SAM10005077/0183 | 2022 | All | All Floors Window sills | Insulation board Throughout |  | Asbestos | Painted/Encapsulated Board | 6 | 3 | 9 | Manage & Inspect
Updated April 2025

## JOHNSTON G BLOCK
BUILDING FREE FROM ACMs

## JOHNSTON HALLS
Previous assessments
All blocks, 3rd to Ground | Stairwell | Panels below windows | 3 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 0 | 2 | 0 | 0 | 0 | 4 | 10 | 2008-04-18 | ACS-MA Chris Lodge PA | N/A | Monitor | Oct 2008
Central building 1st | Roof space plant room | Ceiling | 50 | Amosite/Chrysotile | Encapsulated by Rhodar Nov 09 | 2 | 3 | 2 | 2 | 9 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6 | 15 | 2008-04-18 | ACS-MA Chris Lodge PA | N/A | Full decontamination-area locked for now. | N/A-Locked
Central building 1st | Roof space plant room | Walls | 100 | Amosite/Chrysotile | Encapsulated by Rhodar Nov 09 | 2 | 3 | 2 | 2 | 9 | 1 | 1 | 1 | 2 | 2 | 3 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6 | 15 | 2008-04-18 | ACS-MA Chris Lodge PA | N/A | Full decontamination-area locked for now. | N/A-Locked
Central building 1st | Roof space plant room | Column cladding | 20 | Amosite/Chrysotile | Encapsulated by Rhodar Nov 09 | 2 | 3 | 2 | 2 | 9 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6 | 15 | 2008-04-18 | ACS-MA Chris Lodge PA | N/A | Full decontamination-area locked for now. | N/A-Locked
Central building 1st | Roof space plant room | Ceiling | 50 | Amosite/Chrysotile | Encapsulated by Rhodar Nov 09 Labels & warning signs affixed | 2 | 0 | 0 | 2 | 4 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6 | 10 | 2009-11-25 | CL | 15 |  | May 10
Central building 1st | Roof space plant room | Walls | 100 | Amosite/Chrysotile | Encapsulated by Rhodar Nov 09 Labels & warning signs affixed | 2 | 0 | 0 | 2 | 4 | 1 | 1 | 1 | 2 | 2 | 3 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6 | 10 | 2009-11-25 | CL | 15 |  | May 10
Central building 1st | Roof space plant room | Column cladding | 20 | Amosite/Chrysotile | Encapsulated by Rhodar Nov 09 Labels & warning signs affixed | 2 | 0 | 0 | 2 | 4 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6 | 10 | 2009-11-25 | CL | 15 |  | May 10
Central building 1st | Roof space plant room | Debris beneath tongue & groove wooden floor | 20 | Amosite/Chrysotile | Suspected - no access below floor | 2 | 2 | 2 | 2 | 8 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6 | 14 | 2009-11-25 | CL | N/A |  | May 10
All blocks, 3rd to Ground | Stairwell | Panels below windows | 3 | Amosite | Full building re-survey scheduled for Dec 09 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 0 | 2 | 0 | 0 | 0 | 4 | 10 | 2008-12-18 | Chris Lodge | 10 | Monitor await report Jan 10 | Dec 09
All blocks, 3rd to Ground | Stairwell | Glazed fire doors | Approx 18 doors | Amosite | Full building re-survey scheduled for Dec 09 | 2 | 0 | 0 | 2 | 4 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 7 | 2008-12-18 | Chris Lodge | N/A | Monitor await report Jan 10 | Dec 09
1st | Stairwell D Riser | Debris | 1 | Amosite | Removed by Cape Aug 2010 | 2 | 3 | 2 | 2 | 9 | 1 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 11 | 2010-06-21 | CL | 11 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0260.JPG
2nd | Stairwell F Riser | Debris | 1 | Amosite | Removed by Cape Aug 2010 | 2 | 3 | 2 | 2 | 9 | 1 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 11 | 2010-06-21 | CL | 11 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0119.JPG
3rd | Stairwell F Riser | Debris | 1 | Amosite | Removed by Cape Aug 2010 | 2 | 3 | 2 | 2 | 9 | 1 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 11 | 2010-06-21 | CL | 11 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0116.JPG
1st | EF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS10 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS7 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Loft F | Cement flue | 3 | Chrysotile | Removed by Cape Aug 2010 | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2010-06-21 | CL | 5 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0122.JPG
3rd | Loft F | Redundant cement flue | 2 | Chrysotile | Removed by Cape Aug 2010 | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2010-06-21 | CL | 5 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0123.JPG
3rd | Loft C | Rope on floor | 0.5 | Chrysotile | Removed by Cape Aug 2010 | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2010-06-21 | CL | 4 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0124.JPG
3rd | Loft D | Rope on floor | 0.5 | Chrysotile | Removed by Cape Aug 2010 | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2010-06-21 | CL | 4 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0124.JPG
3rd | Loft F | Rope on floor | 0.5 | Chrysotile | Removed by Cape Aug 2010 | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2010-06-21 | CL | 4 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0124.JPG
1st | AF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF8. | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Store at AF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at BF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at CF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at DF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at EF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at FF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | AS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS10 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS7 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Store at AS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Store at BS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at DS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at ES6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at FS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3-1 | Stairwell A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2010-08-20 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Stairwell F Riser | Board on wall | 1 | Amosite |  | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0117.JPG
3rd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Store at AT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at BT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at CT7 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at DT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at ET6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at FT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Loft A | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2010-06-21 | CL | 5 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
3rd | Loft B | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2010-06-21 | CL | 5 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
3rd | Loft C | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2010-06-21 | CL | 5 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
All | Beneath Concrete floors | AIB Shuttering | 100 | Amosite | Found in AG2 - presumed elsewhere | 2 | 0 | 1 | 2 | 5 | 0 | 0 | 0 | 2 | 0 | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\shuttering.jpg
Grnd | Incinerator Room | Debris in incinerator | 1 | Amosite | Presumed, not able to access inside | 2 | 2 | 2 | 2 | 8 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 4 | 12 | 2010-06-21 | CL | 12 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0412.JPG
1st | AF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF8. | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS10 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS7 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2011-08-15 | CL | 9 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Block C Laundry | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Block F Laundry | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Electric cupboard | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Guest flat bedroom | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Guest flat living room | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Sub-warden bedroom | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Sub-warden living room | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2010-06-21 | CL | 10 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | All Corridors | Fire door internal boarding | 2 | Amosite |  | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 8 | 2010-06-21 | CL | 8 |  | Jul 11 | Images\2010\Johnston Halls Photos\firedoor.jpg
1st | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Store at AF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at BF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at CF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at DF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at EF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at FF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2011-08-15 | CL | 10 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Store at AS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Store at BS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at DS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at ES6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at FS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Stairwell F Riser | Board on wall | 1 | Amosite |  | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0117.JPG
3rd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Store at AT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at BT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at CT7 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at DT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at ET6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at FT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
All | Beneath Concrete floors | AIB Shuttering | 100 | Amosite | Found in AG2 - presumed elsewhere | 2 | 0 | 1 | 2 | 5 | 0 | 0 | 0 | 2 | 0 | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 2011-08-15 | CL | 7 |  | Aug 12 | Images\2010\Johnston Halls Photos\shuttering.jpg
Grnd | Block A ex-calorifier room | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
Grnd | Block F ex-calorifier room | Cement flue | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0414.JPG
Grnd | Incinerator Room F | Cement flue | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0411.JPG
Grnd | Kitchen A Electric cupboard | Ironing board heat mat | 0.5 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0371.JPG
Grnd | Kitchen B cleaners | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
Grnd | Kitchen C cleaners | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
Grnd | Store at AG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at AG5 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at BG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at BG6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at EG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at EG6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at FG5 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2010-06-21 | CL | 7 |  | Jul 11 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Loft A | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2011-08-15 | CL | 5 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
3rd | Loft B | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2011-08-15 | CL | 5 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
3rd | Loft C | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2011-08-15 | CL | 5 |  | Aug 12 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
1st | AF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | AG9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | All Corridors | Fire door internal boarding | 2 | Amosite |  | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 8 | 2012-08-13 | CL | 8 |  | Aug 13 | Images\2010\Johnston Halls Photos\firedoor.jpg
2nd | AS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | AS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | AT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
All | Beneath Concrete floors | AIB Shuttering | 100 | Amosite | Found in AG2 - presumed elsewhere | 2 | 0 | 1 | 2 | 5 | 0 | 0 | 0 | 2 | 0 | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\shuttering.jpg
1st | BF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | BF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | BG9 Kitchen | Kitchen floor tiles | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 8 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Block A ex-calorifier room | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
Grnd | Block C Laundry | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Block F ex-calorifier room | Cement flue | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0414.JPG
Grnd | Block F Laundry | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | BS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | BT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | CF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG6 toilet | Floor Tiles | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 8 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | CG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | CS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | CT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF8. | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | DF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | DG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS10 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | DS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | DT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | EF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | EG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Electric cupboard | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | ES9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | ET9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | FF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | FG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS7 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | FS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2012-08-13 | CL | 9 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | FT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Guest flat bedroom | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Guest flat living room | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Incinerator Room | Debris in incinerator | 1 | Amosite | Presumed, not able to access inside | 2 | 2 | 2 | 2 | 8 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 4 | 12 | 2012-08-13 | CL | 12 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0412.JPG
Grnd | Incinerator Room F | Cement flue | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0411.JPG
1st | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen A Electric cupboard | Ironing board heat mat | 0.5 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0371.JPG
1st | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen B cleaners | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen C cleaners | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
2nd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Loft A | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2012-08-13 | CL | 5 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
3rd | Loft B | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2012-08-13 | CL | 5 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
3rd | Loft C | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2012-08-13 | CL | 5 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0338.JPG
3-1 | Stairwell A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3-1 | Stairwell B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3-1 | Stairwell C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3-1 | Stairwell F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
3rd | Stairwell F Riser | Board on wall | 1 | Amosite |  | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0117.JPG
1st | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
2nd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
3rd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0392.JPG
1st | Store at AF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at AG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at AG5 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at AS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at AT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at BF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at BG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at BG6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at BS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at BT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at CF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at CT7 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at DF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at DS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at DT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at EF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at EG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at EG6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at ES6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at ET6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
1st | Store at FF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Store at FG5 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
2nd | Store at FS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
3rd | Store at FT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2012-08-13 | CL | 7 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0387.JPG
Grnd | Sub-warden bedroom | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
Grnd | Sub-warden living room | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2012-08-13 | CL | 10 |  | Aug 13 | Images\2010\Johnston Halls Photos\1436277_0004.JPG
1st | AF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | AF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG ex-calorifier room | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-02 | C McLeish | 7 |  | June 2016
Grnd | AG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | AG9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | All Corridors | Fire door internal boarding | 2 | Amosite |  | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 8 | 2015-06-02 | C McLeish | 8 |  | June 2016
2nd | AS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | AS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | AT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
All | Beneath Concrete floors | AIB Shuttering | 100 | Amosite | Found in AG2 - presumed elsewhere | 2 | 0 | 1 | 2 | 5 | 0 | 0 | 0 | 2 | 0 | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 2015-06-02 | C McLeish | 7 |  | June 2016
1st | BF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | BF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | BG9 Kitchen | Kitchen floor tiles | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 8 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
2nd | BS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
3rd | BT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
1st | CF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | CF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG Laundry | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | CG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG6 toilet | Floor Tiles | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 8 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | CG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-09 | C McLeish | 9 |  | June 2016
2nd | CS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | CS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | CT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF8. | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | DF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG6 Bedroom | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG6 Sitting room | Panel behind radiator & under sill | 4 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG8 Bedroom | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG8 Kitchen | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG8 Sitting room | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
Grnd | DG9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS10 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-09 | C McLeish | 9 |  | June 2016
2nd | DS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-09 | C McLeish | 9 |  | June 2016
2nd | DS12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
2nd | DS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-09 | C McLeish | 9 |  | June 2016
2nd | DS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
3rd | DT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-09 | C McLeish | 10 |  | June 2016
1st | EF1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
1st | EF6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
1st | EF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | EF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | EG8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Electric cupboard | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | ES1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | ES10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | ES11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | ES12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | ES2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | ES3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | ES4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | ES5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | ES6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | ES7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | ES8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | ES9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | ET2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | ET3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | ET4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | ET5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | ET9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF1 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
1st | FF10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
1st | FF12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
1st | FF5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
1st | FF6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | FF9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG ex-calorifier room | Cement flue | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-02 | C McLeish | 7 |  | June 2016
Grnd | FG Incinerator Room | Debris in incinerator | 1 | Amosite | Presumed, not able to access inside | 2 | 2 | 2 | 2 | 8 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 4 | 12 | 2015-06-17 | C McLeish | 12 |  | June 2016
Grnd | FG Incinerator Room | Cement flue | 2 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | FG Laundry | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-02 | C McLeish | 10 |  | June 2016
Grnd | FG1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG4 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG5 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG6 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG6 (Sub-warden living room) | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG7 (Sub-warden bedroom) | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG8 (Guest flat) bedroom | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | FG8 (Guest flat) living room | Panel behind radiator & under sill | 4 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | FS1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | FS10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | FS11 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | FS12 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | FS2 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | FS2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | FS3 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | FS4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | FS5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | FS6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | FS7 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | FS8 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
2nd | FS9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT1 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT10 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT11 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT12 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT2 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT3 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | FT4 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | FT5 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | FT6 | Panel behind radiator & under sill | 2 | Amosite | Encapsulated by Cape Aug 2010 | 2 | 0 | 1 | 2 | 5 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 9 | 2015-06-17 | C McLeish | 9 |  | June 2016
3rd | FT7 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT8 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | FT9 | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen A Electric cupboard | Ironing board heat mat | 0.5 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen B cleaners | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen C cleaners | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
2nd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
Grnd | Kitchen F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Loft A | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2015-06-17 | C McLeish | 5 |  | June 2016
3rd | Loft B | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2015-06-17 | C McLeish | 5 |  | June 2016
3rd | Loft C | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2015-06-17 | C McLeish | 5 |  | June 2016
3-1 | Stairwell A | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Stairwell A riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3-1 | Stairwell B | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
1st | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Stairwell B riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3-1 | Stairwell C | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3-1 | Stairwell D | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3-1 | Stairwell E | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3-1 | Stairwell F | Panel behind radiator & under sill | 2 | Amosite |  | 2 | 1 | 1 | 2 | 6 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 4 | 10 | 2015-06-17 | C McLeish | 10 |  | June 2016
3rd | Stairwell F Riser | Board on wall | 1 | Amosite |  | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Stariwell C Riser | Rope around Air handling trunking/plant | 1 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Store at AF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | Store at AG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | Store at AG5 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Store at AS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Store at AT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Store at BF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | Store at BG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | Store at BG6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Store at BS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Store at BT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Store at CF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Store at CT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Store at CT7 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Store at DF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Store at DS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Store at DT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Store at EF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | Store at EG1 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | Store at EG6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Store at ES6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Store at ET6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
1st | Store at FF6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
Grnd | Store at FG5 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
2nd | Store at FS6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
3rd | Store at FT6 | Vinyl floor tiles | 3 | Chrysotile |  | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 7 | 2015-06-17 | C McLeish | 7 |  | June 2016
BUILDING FREE FROM ACMs - TO BE DEMOLISHED
BUILDING FREE FROM ACMs
TO BE DEMOLISHED

## JOHNSTON REFECTORY
BUILDING FREE FROM ACMs
TO BE DEMOLISHED

## KEITH HOUSE
Updated April 2025
All items removed 2024

## KINGS COLLEGE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Kings Colllege | Basement | Plantroom KCB 1 | Pipe gaskets | 2 | Chrysotile |  | 4 | 5 | 9 | Manage & reinspect
| Kings Colllege | Basement | KCB3 | Distribution Boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone Hall AHU plantroom | Paper beneath fibreglass pipe insulation | 15 | Chrysotile |  | 5 | 4 | 9 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone Hall plant room | Ceiling panelling in undercroft | 1 | Chrysotile |  | 5 | 4 | 9 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone Hall plant room | Insulation debris to walls | 1 | Chrysotile | Cleaned by Cape Mar 11-painted & labelled | 5 | 4 | 9 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone Main Gas Cock | Rope to Electrics | 1 | Chrysotile |  | 5 | 3 | 8 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone Hall plant room | Pipe gaskets | 1 | Chrysotile |  | 4 | 4 | 8 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone Kitchen wine store | Floor tiles | 20 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone wine store | Cold room panels | 10 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone paper Store 1 | Cream vinyl floor tiles | 40 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone Paper Store 2 | Grey floor tiles | 20 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone paper Store 3 | Grey floor tiles | 20 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Kings Colllege | Basement | Elphinstone paper Store 4 | Grey floor tiles | 20 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Kings Colllege | Basement | X018 Switchgear | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | Basement | X024 Plant room | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | Ground | KCG 14 | Insulation to pipe in corner | 5 | Chrysotile | Cleaned & encapsulated by Cape Sep 2010 | 5 | 3 | 8 | Manage & reinspect
| Kings Colllege | Ground | Linklater Room 1 | Panel behind radiators | 8 | Chrysotile |  | 4 | 5 | 9 | Manage & reinspect
| Kings Colllege | Ground | Linklater Room 2 | Panel behind radiators | 8 | Chrysotile |  | 4 | 5 | 9 | Manage & reinspect
| Kings Colllege | Ground | Stairwell to Divinity Library | Black marbled floor screed | 20 | Anthophyllite |  | 4 | 5 | 9 | Manage & reinspect
| Kings Colllege | Ground | KCG 5 | Stair nosing | 1 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
| Kings Colllege | Ground | Elphinstone kitchen | Grey stair nosing | 1 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
| Kings Colllege | Ground | Stairwell outside KCG 5 | Black marbled floor screed | 20 | Anthophyllite |  | 4 | 4 | 8 | Manage & reinspect
| Kings Colllege | Ground | Stairwell next to KCG 8 | Black marbled floor screed | 20 | Anthophyllite |  | 4 | 4 | 8 | Manage & reinspect
| Kings Colllege | Ground | Elphinstone Hall | Panel behind radiators | 30 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Kings Colllege | Ground | Elphinstone Hall Servery corridor | Black & grey vinyl floor tiles | 35 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Kings Colllege | Ground | KCG14 | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | Ground | KQG 1 electrical cupboard | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | Ground | X002 Cleaners store | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | Ground | Elphinstone hall ante room electrical cupboard | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | Ground | Conference projector room Electrical cupboard | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Kings Colllege | 1st | Corridor outside KCF 22 | Stair nosing | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Kings Colllege | 2nd | Link Corridor - fuse box | Cloth to fuse holder | 1 | Chrysotile | Needs sampled | 5 | 4 | 9 | Manage & reinspect
| Kings Colllege | 2nd | Corridor | Rope seals to skylights | 2 | Chrysotile |  | 5 | 4 | 9 | Manage & reinspect
| Kings Colllege | 2nd | Special Collections - lift motor room | Gaskets to lift machinery | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Kings Colllege |  | KCS3 | Distribution boards | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
Updated April 2025

## KINGS PAVILION
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1363626-0090 | Kings Pavilion Type 2 2009.pdf | Underfloor | Swimming pool duct | Large & small bore cement pipes | 100 | Chrysotile |  | 4 | 1 | 5 | Manage & Reinspect
1363626-0035 | Kings Pavilion Type 2 2009.pdf | Ground | Attendants Office | Pipework flange gaskets | 1 | Chrysotile |  | 4 | 5 | 9 | Manage & Reinspect
1363626-0078 | Kings Pavilion Type 2 2009.pdf | Ground | Female changing WC store | Electrics-flash guards | 1 | Chrysotile | Needs sampled | 4 | 5 | 9 | Manage & Reinspect
1363626-0077 | Kings Pavilion Type 2 2009.pdf | Ground, external | Store 2 | Cladding above door | 3 | Chrysotile | Painted by Cape Mar 11 | 3 | 0 | 3 | Manage & Reinspect
1363626-0021 | Kings Pavilion Type 2 2009.pdf | 1st | Fitness suite | Textured coating within ceiling void | 50 | Chrysotile |  | 4 | 5 | 9 | Manage & Reinspect
Updated April 2025

## KINGS PAVILION FLAT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1367533-0001 | Kings Pavilion Flat Type 2 2009.pdf | Ground | Entrance | Fuseboard | 1 | Chrysotile | Needs sampled | 4 | 5 | 9 | Manage & Reinspect
Updated April 2025

## LIBERTY BUILDING
No asbestos in this building - report 2007

## LILIAN SUTTON
No asbestos in this building

## MacROBERT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
? | Unknown | External | Rear Fire Escape deck over plantroom | Asbestos board packer beneath cladding | 50 | Amosite | Presumed | 5 | 2 | 7 | Only accessible if wall demolished
AP001785-03-13/0033 | MacRobert 2018 | 9 | Ceiling | Cut off cement sleeve to ceiling | 1 | Chrysotile | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0005 | MacRobert 2018 | 9 | Lift Motor rooms 1 & 2 | Brake shoes to lift gear | 10 | Chrysotile | Presumed, but probably non-asbestos | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0049 | MacRobert 2018 | 8 | Ceiling at photo copy door - 833 on survey | Cement screed | 2m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-03-13/0051 | MacRobert 2018 | 8 | Ceiling above cable tray - room 834 store | Cement screed | 2m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0037 | MacRobert 2018 | 8 | Ceiling void in corridor between offices 818 & 812 | Cement screed | 5m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
? | Resurvey 2022 | 8 | Room 809 | Debris and screed | 5m | Cement | clean | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0078 | MacRobert 2018 | 7 | Ceiling void above door - store room 727 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0112 | MacRobert 2018 | 7 | Ceiling void above right hand side lift - at WC room 713 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0113 | MacRobert 2018 | 7 | Ceiling void above door on right hand side wall - room 709 | Cement screed | 4m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0072 | MacRobert 2018 | 7 | Ceiling void above door on left hand side wall - room 709a | Cement screed | 4m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0125 | MacRobert 2018 | 6 | Ceiling void in corridor at wall of location store 634 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0129 | MacRobert 2018 | 6 | Ceiling void in middle of room 632 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0144 | MacRobert 2018 | 6 | Ceiling void above door in room 624 - hub | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0131 | MacRobert 2018 | 6 | Ceiling void above door in room 627 - store | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0135 | MacRobert 2018 | 6 | Ceiling void in middle of room 623 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0464 | MacRobert 2018 | 6 | Ceiling - room 614 | Presumed as painted | 30m | Cement | Don’t drill in-between support beams | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0157 | MacRobert 2018 | 6 | Ceiling void in middle of room 611 - WC | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0155 | MacRobert 2018 | 6 | Ceiling void in middle of room 609 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0147 | MacRobert 2018 | 6 | Ceiling void in middle of room 601 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0164 | MacRobert 2018 | 5 | Ceiling void above seating area room - main foyer | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0167 | MacRobert 2018 | 5 | Ceiling void above the desk area room above - coffee area | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0166 | MacRobert 2018 | 5 | Ceiling void between locations 520 & 521 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0194 | MacRobert 2018 | 5 | Ceiling void within cracks in the columns - room 508 | Loose insulation | 1m | Insulation residue | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0191 | MacRobert 2018 | 5 | Ceiling void within cracks in the columns - room 505 | Loose insulation | 1m | Insulation residue | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0205 | MacRobert 2018 | 4 | Ceiling void above door of female toilets - foyer at triplex lifts | Cement screed | 2m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0215 | MacRobert 2018 | 4 | Ceiling void running from door to window wall in room 427 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0206 | MacRobert 2018 | 4 | Ceiling void above door of location - outside room 421 | Cement screed | 2m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0208 | MacRobert 2018 | 4 | Ceiling void above door of location - in corridor between room 403 and 431 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0242 | MacRobert 2018 | 4 | Ceiling void at left hand side of door - in corridor between 406 and 427 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0208 | MacRobert 2018 | 3 | Ceiling void throughout corridor - between 304 and 310 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0242 | MacRobert 2018 | 3 | Ceiling void throughout corridor - between 303 and 314 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0265 | MacRobert 2018 | 3 | Ceiling void throughout corridor - between 302 and 317 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
| Resurvey 2022 |  | Room 268 | Cement screed | 60m | Cement | Needs cleaned | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0266 | MacRobert 2018 | 2 | Ceiling void between rooms 256 & 257 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0267 | MacRobert 2018 | 2 | Ceiling void from entrance of lift corridor - between 253 and 261 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0212 | MacRobert 2018 | 2 | Ceiling void from entrance at staff lift - between 252 and 265 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0331 | MacRobert 2018 | 2 | Ceiling void to left of door - outside room 250 | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0332 | MacRobert 2018 | 1 | Ceiling void - room 115, cleaners | Cement screed | 1m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0277 | MacRobert 2018 | 1 | Ceiling void - room 114 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0378 | MacRobert 2018 | Ground | Pipe bracket within void area - stair landing - North East | Cloth | 1 | Cloth | Remove | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0383 | MacRobert 2018 | Ground | Wall to left of door - duct 057 | Insulation residue | 4m | Insulation residue | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0437 | MacRobert 2018 | Ground | Ceiling - room 024 | Cement screed | 3m | Cement | Encapsulated and labelled | 5 | 2 | 7 | Manage & reinspect
AP001785-0313/0171 | MacRobert 2018 | Ground | Wall to right of door above electrics. | Red Mastic | 1m | Mastic | Remove | 5 | 2 | 7 | Manage & reinspect
Updated April 2025

## MARISCHAL COLLEGE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Marischal College | First Basement | Duct from Corridor to old boiler house | Insulation debris on floor | 50 | Amosite & Chrysotile | Area locked off | 11 | 2 | 13 | Area is locked off until cleaning takes place
| Marischal College | First Basement | Duct from Corridor to old boiler house | Insulation debris on floor | 50 | Amosite & Chrysotile | Area locked off | 11 | 2 | 13 | Area is locked off until cleaning takes place
| Marischal College | First Basement | Duct from Corridor to old boiler house | Pipe insulation adjacent to old boiler room | 50 | Amosite & Chrysotile | Area locked off | 11 | 2 | 13 | Area is locked off until cleaning takes place
| Marischal College | First Basement | Duct from Corridor to old boiler house | Debris on floor adjacent to old boiler room entrance | 50 | Amosite & Chrysotile | Area locked off | 11 | 2 | 13 | Area is locked off until cleaning takes place
| Marischal College | First Basement | Duct from Corridor to old boiler house | Debris from looped section of duct | 50 | Amosite & Chrysotile | Area locked off | 11 | 2 | 13 | Area is locked off until cleaning takes place
| Marischal College | First Basement | Duct from Corridor to old boiler house | Dust sample from looped section of duct | 50 | Amosite & Chrysotile | Area locked off | 11 | 2 | 13 | Area is locked off until cleaning takes place
| Marischal College | First Basement | -1/009 Main switch room | Residue to walls & girders | 12 | Amosite & Chrysotile | Cleaned by Cape April 2014 caveat in 4SC to advise reverse side of boards may be contaminated | 11 | 3 | 14 | Area is locked off until cleaning takes place
| Marischal College | First Basement | Anatomy Workshop | Fuseboard flashguards | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Marischal College | First Basement | Anatomy corridor duct | Insulation to pipe brackets | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Marischal College | First Basement | Lobby adj. main switchroom (anatomy) | Insulation to pipe brackets | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Marischal College | First Basement | New Boiler House (No.1) | Gaskets to pumps | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Marischal College | First Basement | New Boiler House (No.1) | Gaskets to boilers | 1 | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Marischal College | Second Basement | Anatomy Calorifier room | Debris to calorifier under MMMF | 2 | Amosite & Chrysotile |  | 9 | 1 | 10 | Maintain until removal
| Marischal College | Second Basement | Anatomy Calorifier room | Gasket to calorifier | 0.5 | Chrysotile |  | 5 | 1 | 6 | Maintain until removal
| Marischal College | Second Basement | Anatomy embalming room | Washers to wall heater | 0.5 | Chrysotile |  | 5 | 0 | 5 | Manage & reinspect
| Marischal College | Second Basement | Anatomy external gas meter | Gaskets | 1 | Chrysotile |  | 6 | 2 | 8 | Manage & reinspect
| Marischal College | Ground | Museum Ventilation plantroom | Sealant to ducting | 3 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Marischal College | Ground | Anatomy Office | Sealant to ducting | 1 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Marischal College | Ground | Anatomy WC (Facing WN Street) | Cistern & seat | 1 | Crocidolite & Amosite |  | 4 | 2 | 6 | Manage & reinspect
| Marischal College | Ground | Anatomy Kitchen | Sink mat | 1 | Chrysotile |  | 3 | 0 | 3 | Manage & reinspect
| Marischal College | Ground | Museum store (new) | Stair nosing | 5 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
| Marischal College | Ground | Museum store mezzanine | Stair nosing | 7 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
| Marischal College | Ground | Museum store | Stair nosing | 7 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
| Marischal College | Ground | Museum store | Stair nosing | 40 | Chrysotile |  | 3 | 5 | 8 | Manage & reinspect
| Marischal College | Ground | Mezzanine WC | Cistern & seat | 1 | Crocidolite & Amosite |  | 4 | 2 | 6 | Manage & reinspect
| Marischal College | 1st | Stairwell (West) | Seal to cast iron pipe | 1 | Amosite |  | 7 | 1 | 8 | Manage & reinspect
| Marischal College | 1st | Mezzanine Projection room | Stair nosing | 1 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Marischal College | 1st | Kitchen | Beam cladding | 5 | Chrysotile |  | 4 | 2 | 6 | Manage & reinspect
| Marischal College | 1st | Stairwell WC (East) | Cistern & seat | 1 | Chrysotile |  | 2 | 2 | 4 | Manage & reinspect
| Marischal College | 1st | Mezzanine store | Stair nosing | 1 | Chrysotile |  | 2 | 1 | 3 | Manage & reinspect
| Marischal College | 1st | Conservation lab | Stair nosing | 2 | Chrysotile |  | 2 | 1 | 3 | Manage & reinspect
| Marischal College | 2nd | Mitchell Hall landing lobby | Stair nosing | 100 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Marischal College | 2nd | Front west stairs | Stair nosing | 15 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Marischal College | 2nd | Front east stairs | Stair nosing | 15 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| Marischal College | External | Stairs adjacent Porters | High level pipe insulation | 4 | Crocidolite & Amosite |  | 7 | 2 | 9 | Manage & reinspect
| Marischal College | External | Lecture theatre fire escape | Synthetic slates | 24 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
| Marischal College | External | Lecture theatre fire escape | Corrugated sheeting | 18 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
| Marischal College | External | Lecture theatre fire escape | Cement gutterring | 3 | Chrysotile |  | 4 | 1 | 5 | Manage & reinspect
Updated April 2025

## MATERNITY HOSPITAL
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Maternity Hospital | 2nd | Loft | Paper insulation beneath MMMF pipe insulation | 60 | Chrysotile | Section of loft & pipe insulation removed above Rms 7, 9, 11 and connecting corridor | 7 | 2 | 9 | Monitor
| Maternity Hospital | 2nd | WC 44 | Toilet cistern & seat | 2 | Amosite |  | 4 | 4 | 8 | Monitor
| Maternity Hospital | 2nd | WC 1 | Toilet cistern & seat | 2 | Amosite |  | 4 | 4 | 8 | Monitor
| Maternity Hospital | 2nd | Stairwell 2 | Nosing strips | 50 | Chrysotile |  | 3 | 4 | 7 | Monitor
| Maternity Hospital | 2nd | Stairwell 1 | Nosing strips | 50 | Chrysotile |  | 3 | 4 | 7 | Monitor
| Maternity Hospital | 2nd | Room 13 | Cement panel under radiator shelf | 2 | Chrysotile |  | 3 | 4 | 7 | Monitor
| Maternity Hospital | 2nd | Room 12 | Cement panel under radiator shelf | 2 | Chrysotile |  | 3 | 4 | 7 | Monitor
| Maternity Hospital | 2nd | Stairwell 1 | Cement panel under radiator shelf | 2 | Chrysotile |  | 3 | 3 | 6 | Monitor
| Maternity Hospital | 2nd | Room 18 | Under-sink mat | 1 | Chrysotile |  | 2 | 4 | 6 | Monitor
| Maternity Hospital | 2nd | Room 15 | Under-sink mat | 1 | Chrysotile |  | 2 | 4 | 6 | Monitor
| Maternity Hospital | 2nd | Room 14 | Under-sink mat | 1 | Chrysotile |  | 2 | 4 | 6 | Monitor
| Maternity Hospital | 2nd | Room 11 | Under-sink mat | 1 | Chrysotile |  | 2 | 4 | 6 | Monitor
| Maternity Hospital | 2nd | Room 10 | Under-sink mat | 1 | Chrysotile |  | 2 | 4 | 6 | Monitor
| Maternity Hospital | 2nd | Loft lift motor room | Brake shoes | 1 | Chrysotile | Needs sampled | 3 | 3 | 6 | Monitor
| Maternity Hospital | 2nd | Roof, external | Cement cowl | 1 | Chrysotile | Needs sampled | 3 | 0 | 3 | Monitor
What access and responsibility do we have for this building?
Updated April 2025

## MEDICAL SCHOOL LIBRARY
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Med School | Ground | Compactus Shelving | Infill panel over door | 1.5 | Amosite | Paint coat touched up as required | 4 | 5 | 9 | Manage & reinspect
| Med School | Ground | Cleaners Cupboard | Infill panel over door | 1 | Amosite | Paint coat touched up as required-labelled | 4 | 4 | 8 | Manage & reinspect
| Med School | Ground | Cleaners Cupboard | Gaskets to pipework | 1 | Chrysotile |  | 3 | 3 | 6 | Manage & reinspect
| Med School | 1st | Reading Room | Infill panel over door | 1.5 | Amosite | Paint coat touched up as required | 4 | 5 | 9 | Manage & reinspect
| Med School | 1st | Reading Room | Entrance from corridor - infill panel over door | 3 | Amosite | Paint coat touched up as required | 4 | 5 | 9 | Manage & reinspect
| Med School | 1st | Rear fire stairs | Infill panel over door | 2 | Amosite | Paint coat touched up as required | 4 | 4 | 8 | Manage & reinspect
| Med School | 1st | Cleaners Cupboard | Infill panel over door | 2 | Amosite | Paint coat touched up as required-labelled | 4 | 4 | 8 | Manage & reinspect
| Med School | 2nd | Cleaners Cupboard | Infill panel over door | 1 | Amosite | Paint coat touched up as required-labelled minor gouge possible from ladder | 4 | 4 | 8 | Manage & reinspect
| Med School | 2nd | Reading Room | Infill panel over door | 1.5 | Amosite | Paint coat touched up as required | 4 | 5 | 9 | Manage & reinspect
| Med School | 2nd | Rear fire stairs | Infill panel over door | 1 | Amosite | Paint coat touched up as required | 4 | 4 | 8 | Manage & reinspect
| Med School | 3rd | Rear fire stairs | Infill panel over door | 1 | Amosite | Paint coat touched up as required | 4 | 4 | 8 | Manage & reinspect
| Med School | 3rd | Cleaners Cupboard | Infill panel over door | 1 | Amosite | Paint coat touched up as required-labelled | 4 | 4 | 8 | Manage & reinspect
| Med School | Roof | Ventilation Room 1 | Panel on wall 4 adj. Ventilation Rm 2 | 3 | Amosite | Encapsulated & labelled by Cape Sep 10 | 5 | 5 | 10 | Manage & reinspect
| Med School | Roof | Ventilation Room 1 | Metal downpipe joints-insulation | 10 | Amosite | Encapsulated & labelled by Cape Sep 09 | 6 | 3 | 9 | Manage & reinspect
| Med School | Roof | Ventilation Room 1 | AHU - rope seals to ducting | 2 | Chrysotile | Paint coat touched up as required | 4 | 5 | 9 | Manage & reinspect
| Med School | Roof | Ventilation Room 2 | Panelling to external walls | 30 | Amosite | Encapsulated & labelled by Cape Sep 10 | 5 | 5 | 10 | Manage & reinspect
| Med School | Roof | Lift motor room | Infill panel over door | 0.25 | Amosite | Encapsulated & labelled by Cape Sep 09 | 5 | 3 | 8 | Manage & reinspect
Updated April 2025

## MESTON BUILDING
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Meston | Basement | Compressor plantroom | Pipework hanger gaskets | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | Basement | Compressor plantroom | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | Basement | Corridor 1 | Pipe insulation above entrance door | 8 | Amosite | Repaired by Cape Sep 10 | 7 | 4 | 11
| Meston | Basement | Corridor 1 | Pipe insulation | 20 | Amosite | Repaired by Cape Sep 10 | 7 | 4 | 11
| Meston | Basement | Corridor 1 | Small bore pipework | 8 | Amosite | Repaired by Cape Sep 10 | 7 | 4 | 11
| Meston | Basement | Corridor 1 | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | Basement | Corridor 2 | Pipe insulation | 16 | Amosite |  | 7 | 3 | 10
| Meston | Basement | Corridor 2 | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | Basement | Corridor 3 | Panel over fire door to Corridor 2 | 2 | Amosite | Painted & labelled by Cape Dec 09 | 6 | 4 | 10
| Meston | Basement | Corridor 3 | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | Basement | Lecture theatre B58 | Fume cabinet lining | 2 | Amosite |  | 6 | 6 | 12
| Meston | Basement | Lecture theatre B58 | Square profile AIB duct in void to fume cabinet | 8 | Amosite |  | 6 | 6 | 12
| Meston | Basement | Lecture theatre B58 | Riser panel | 2 | Amosite |  | 6 | 5 | 11
| Meston | Basement | Lecture theatre B58 | Riser panel on wall next to fire exit | 2 | Amosite |  | 6 | 5 | 11
| Meston | Basement | Lecture theatre B58 | Stairs to Projection room-nosing strip | 4 | Chrysotile |  | 2 | 6 | 8
| Meston | Basement | Room B53a | Square profile AIB duct in void to fume cabinets | 6 | Amosite | Originally missed by Nat Brit | 6 | 5 | 11
| Meston | Basement | Room B53a | Fume cabinet lining | 6 | Chrysotile |  | 4 | 5 | 9
| Meston | Basement | Room B57 | Suspended ceiling tiles | 15 | Amosite |  | 6 | 6 | 12
| Meston | Basement | Room B57 Service duct | Cloth packer to pipe hangers | 1 | Chrysotile | Painted by Pyeroy Dec 2009 | 3 | 1 | 4
| Meston | Basement | Room B57 Service duct | Cement flue | 30 | Chrysotile | Painted by Pyeroy Dec 2009 | 2 | 2 | 4
| Meston | Basement | Room B61 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 5 | 11
| Meston | Basement | Room B64 | Pipe insulation to nearest wall | 15 | Amosite | Encapsulated by Cape Sep 10 | 6 | 4 | 10
| Meston | Basement | Room B65 | Insulating panel at floor level | 1 | Amosite |  | 6 | 3 | 9
| Meston | Basement | Room B65 | Insulating panel at high level | 1 | Amosite |  | 6 | 3 | 9
| Meston | Basement | Room B66 | Insulating board in ceiling void | 1 | Amosite | Encapsulated by Rhodar 2008 | 5 | 3 | 8
| Meston | Basement | Room B67a | Cement lining to equipment | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Basement | Room B68 | Pipework gaskets | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Basement | Room B68 | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Basement | Room B76 | Pipe insulation above entrance door to the right | 4 | Amosite | Approx. 8m removed by Cape March 09 | 7 | 4 | 11
| Meston | Basement | Room B76 | Small bore pipe above counter-insulation | 2 | Amosite | Encapsulated by Cape Sep 10 | 6 | 4 | 10
| Meston | Basement | Room B76 | Small bore pipe above counter-insulation to the left hand side | 2 | Amosite | Encapsulated by Cape Sep 10 | 6 | 4 | 10
| Meston | Basement | Room B76 | Pipe insulation above window | 8 | Amosite | Encapsulated by Cape Sep 10 | 6 | 4 | 10
| Meston | Basement | Room B76 | Pipe insulation along wall above windows | 6 | Amosite | Encapsulated by Cape Sep 10 | 6 | 4 | 10
| Meston | Basement | Room B76 | Insulating board flue above chemical cabinet | 2 | Amosite | Labelled | 6 | 4 | 10
| Meston | Basement | Room B76 | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | Basement | Room B76 | Gas pipe flanges gasket | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | Basement | Room B76 | Chemical cabinet cement lining | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | Basement | Room B76 Riser duct | Pipe insulation | 4 | Amosite | Stripped by Pyeroy Dec 09 - exposed end to Chemical Store encapsulated | 7 | 4 | 11
| Meston | Basement | Sub-station | Cement infill panels to vents | 1 | Chrysotile |  | 4 | 3 | 7
| Meston | Lower Ground | Chemistry Entrance Lobby ceiling void | AIB wall panelling above small hatches in wooden ceiling | 16 | Amosite | Encapsulated & labelled by Pyeroy Dec 10 | 6 | 4 | 10
| Meston | Lower Ground | Cleaners Store | Suspended ceiling tiles | 4 | Amosite | Repaired by Cape Dec 09 | 6 | 4 | 10
| Meston | Lower Ground | Cleaners store | Suspended ceiling tiles | 4 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Cleaners Store | WC cistern on wall | 1 | Amosite |  | 4 | 3 | 7
| Meston | Lower Ground | Cleaners store | WC cistern on wall | 1 | Amosite |  | 2 | 3 | 5
| Meston | Lower Ground | Corridor 2 | Cloth flash guards | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | Lower Ground | Corridor 2 | Electrical box cement panels | 1 | Chrysotile |  | 4 | 3 | 7
| Meston | Lower Ground | Corridor 3 | Cloth flash guards to electrical box | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | Lower Ground | Corridor 3 | Electrical box cement panels | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | Lower Ground | Corridor 3 adj Room 20 | Pipe Insulation | 6 | Amosite |  | 8 | 4 | 12
| Meston | Lower Ground | Corridor 3 O/S 024 | Cupboard doors | 4 | Chrysotile | Encapsulated by Cape Jul 11 | 4 | 3 | 7
| Meston | Lower Ground | Corridor 3 | Ceiling Pipe elbow bends | 5 | Amosite |  | 9 | 4 | 13
| Meston | Lower Ground | Corridor 4 | High level pipe leading to plantroom | 8 | Amosite | Labelled | 8 | 4 | 12
| Meston | Lower Ground | Corridor 5 stairs | Black vinyl floor tiles | 8 | Chrysotile |  | 2 | 4 | 6
| Meston | Lower Ground | Corridor 5 stairs | Stair nosing strips | 4 | Chrysotile |  | 2 | 4 | 6
| Meston | Lower Ground | Corridor 6 | Suspended ceiling tiles | 40 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Corridor 7 | Suspended ceiling tiles | 40 | Amosite | Repaired by Cape Dec 09. 2 rows prior to fire door are non-asbestos | 5 | 5 | 10
| Meston | Lower Ground | Corridor 7 adj Ice machine | Suspended ceiling tiles | 8 | Amosite | Repaired by Cape Dec 09 | 6 | 4 | 10
| Meston | Lower Ground | Electrical store adjacent Room 059 | Suspended ceiling tiles | 8 | Amosite | Repaired by Cape Dec 09 | 5 | 5 | 10
| Meston | Lower Ground | Electrical store adjacent Room 068 | Cloth flash guards to electrical box | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | Lower Ground | Electrical store adjacent Room 068 | Suspended ceiling tiles | 6 | Amosite | Encapsulated by Cape Nov 09 | 4 | 2 | 6
| Meston | Lower Ground | Female WC | Suspended ceiling tiles | 20 | Amosite |  | 6 | 5 | 11
| Meston | Lower Ground | Female WC | Ceiling upstand | 10 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Female WC | Soffit above windows | 10 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Female WC | Heating boxing below windows | 10 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | LT4 Plantroom | Remnants of pipe insulation in ceiling | 1 | Amosite | Encapsulated by Rhodar April 2009 | 7 | 3 | 10 | Manage
| Meston | Lower Ground | Main North Plantroom | Suspected insulation debris to pipework (Under MMMF insulation) | 10 | Amosite | No uncontrolled removal permitted | 7 | 3 | 10 | Monitor
| Meston | Lower Ground | Male WC | Suspended ceiling tiles | 20 | Amosite |  | 6 | 5 | 11
| Meston | Lower Ground | Male WC | Ceiling upstand | 10 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Male WC | Soffit above windows | 10 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Male WC | Heating boxing below windows | 10 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Old 'Toxic Lab' Plantroom | Exhaust pipe gasket | 1 | Chrysotile | Encapsulated by Rhodar 2008 | 4 | 2 | 6
| Meston | Lower Ground | Old 'Toxic Lab' Plantroom | Cloth packer to pipe hangers | 1 | Chrysotile | Encapsulated by Rhodar 2008 | 4 | 2 | 6
| Meston | Lower Ground | Old 'Toxic Lab' Plantroom | Cloth flashguards | 1 | Chrysotile |  | 4 | 2 | 6
| Meston | Lower Ground | Plantroom adj Room 12 | Rope seal to ventilation ducting | 2 | Chrysotile |  | 5 | 3 | 8
| Meston | Lower Ground | Plantroom adj Room 12 | Ventilation ducting-cement cladding | 5 | Chrysotile |  | 4 | 3 | 7
| Meston | Lower Ground | Riser opposite 023 | Pipe insulation & debris | 5 | Amosite | Riser is padlocked off. | 11 | 2 | 13
| Meston | Lower Ground | Riser adjacent to Room 18 | Pipe insulation & debris | 5 | Amosite | Riser is padlocked off. | 11 | 2 | 13
| Meston | Lower Ground | Room 001 | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 3 | 5
| Meston | Lower Ground | Room 002 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | Lower Ground | Room 023 | Cloth flash guards | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Lower Ground | Room 023a | Insulating board to top of fume cabinet | 2 | Amosite |  | 6 | 5 | 11
| Meston | Lower Ground | Room 023a | Oven rope seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Lower Ground | Room 023a | Cement flue | 8 | Chrysotile |  | 4 | 5 | 9
| Meston | Lower Ground | Room 027 | Insulation debris within ceiling void above office | 3 | Amosite |  | 11 | 4 | 15 | Remediate
| Meston | Lower Ground | Room 027 | Cloth flash guards | 1 | Chrysotile |  | 5 | 6 | 11
| Meston | Lower Ground | Room 027 | Gallenkamp oven seal | 1 | Chrysotile | Encapsulated | 4 | 6 | 10
| Meston | Lower Ground | Room 027 Plantroom | Presumed debris under plant - inaccessible | 5 | Amosite | Cleaned by Rhodar Nov 09 | 5 | 3 | 8 | No uncontrolled removal
| Meston | Lower Ground | Room 054 | Insulating board boxing to window column | 4 | Amosite | Painted by Cape Sep 12 | 5 | 5 | 10
| Meston | Lower Ground | Room 056 | Insulating board boxing | 4 | Amosite | Painted by Cape April 16 | 6 | 5 | 11
| Meston | Lower Ground | Room 057 | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | Lower Ground | Room 058 LT4 | Vertical pillar cladding | 10 | Amosite | 2 strips | 6 | 5 | 11
| Meston | Lower Ground | Room 058 LT4 | Fume cabinet lining | 5 | Chrysotile |  | 4 | 6 | 10
| Meston | Lower Ground | Room 059 | Suspended ceiling tiles | 18 | Amosite |  | 6 | 6 | 12
| Meston | Lower Ground | Room 059 | Heating boxing below windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 059 | Soffit above windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 059 | Cement Flue in ceiling void | 10 | Chrysotile | Presumed | 4 | 1 | 5
| Meston | Lower Ground | Room 059 | Ceiling upstand | 9 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 059d | Suspended ceiling tiles | 12 | Amosite |  | 6 | 6 | 12
| Meston | Lower Ground | Room 059d | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 059d | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 059d | Heating boxing below windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 059d WC | Suspended ceiling tiles | 2 | Amosite |  | 6 | 5 | 11
| Meston | Lower Ground | Room 060 | Suspended ceiling tiles | 14 | Amosite |  | 6 | 6 | 12
| Meston | Lower Ground | Room 060 | Soffit above windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 060 | Ceiling upstand | 7 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 060 | Heating boxing below windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 060 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 060 Riser | Boxing around flue pipe | 4 | Amosite | Riser decontaminated by Cape April 2010. | 5 | 3 | 8
| Meston | Lower Ground | Room 060 Riser | Suspended ceiling tiles | 1 | Amosite | Riser decontaminated by Cape April 2010. Tiles encapsulated | 5 | 2 | 7
| Meston | Lower Ground | Room 060 Riser | Cement flue pipes | 40 | Chrysotile | Riser decontaminated by Cape April 2010. | 3 | 3 | 6
| Meston | Lower Ground | Room 065 | Suspended ceiling tiles | 12 | Amosite |  | 6 | 6 | 12
| Meston | Lower Ground | Room 065 | Heating boxing below windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 065 | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 065 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 065 | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 4 | 6
| Meston | Lower Ground | Room 065a | Suspended ceiling tiles | 12 | Amosite |  | 6 | 6 | 12
| Meston | Lower Ground | Room 065a | Heating boxing below windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 065a | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 065a | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 066 | Suspended ceiling tiles | 12 | Amosite | 2 Cracked tiles need paint & repair | 6 | 6 | 12
| Meston | Lower Ground | Room 066a | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 066a | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 068 | Suspended ceiling tiles | 6 | Amosite | Repaired by Cape Apr 2010 | 5 | 4 | 9
| Meston | Lower Ground | Room 069 | Suspended ceiling tiles | 6 | Amosite | Missing tile replaced and minor repiar, by Cape Sep 12 | 5 | 5 | 10
| Meston | Lower Ground | Room 069 Service duct | Insulating board on wall behind electrical boxes | 1 | Amosite | Encapsulated By Pyeroy Dec 09 | 4 | 3 | 7
| Meston | Lower Ground | Room 069 Service duct | Cloth packer to pipe hangers | 1 | Chrysotile | Encapsulated By Pyeroy Dec 09 | 3 | 3 | 6
| Meston | Lower Ground | Room 069 Service duct | Fire door panel | 2 | Amosite | Encapsulated By Pyeroy Dec 09 | 4 | 3 | 7
| Meston | Lower Ground | Room 069 Service duct | Cement flue pipes | 20 | Chrysotile | Encapsulated By Pyeroy Dec 09 | 2 | 3 | 5
| Meston | Lower Ground | Room 071 | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 3 | 5
| Meston | Lower Ground | Room 072a | Insulation board in ceiling void | 4 | Amosite | Encapsulated by Cape Jun 10 During an environmental clean of ceiling void | 4 | 5 | 9
| Meston | Lower Ground | Room 072a | Cement sheet in void above beams | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | Lower Ground | Room 075 and into corridor | Round profile AC ducting to fume cabinets in ceiling void | 20 | Chrysotile | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 4 | 4 | 8
| Meston | Lower Ground | Room 076 | AC lining to 11 remaining fume cabinets | 50 | Chrysotile |  | 4 | 7 | 11
| Meston | Lower Ground | Room 076 | Shuttering marks to concrete ceiling | 5 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 4 | 4 | 8
| Meston | Lower Ground | Room 076 | AIB packers to 1no. Concrete window columns | 1 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 4 | 4 | 8
| Meston | Lower Ground | Room 076 | Woven pipe hanger packers throughout ceiling void. | 5 | Chrysotile | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 2 | 4 | 6
| Meston | Lower Ground | Room 078 | Square profile AIB ducting to fume cabinets in ceiling void | 10 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 6 | 4 | 10
| Meston | Lower Ground | Room 078 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 6 | 10
| Meston | Lower Ground | Room 078 Bio-Discovery Fire Stairs | AIB high level walls panels around fire exit (in ceiling void) Both sides | 10 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 5 | 4 | 9
| Meston | Lower Ground | Room 079 | Fume cabinet lining | 10 | Chrysotile |  | 4 | 6 | 10
| Meston | Lower Ground | Room 079 | AIB packers to 1no. Concrete window columns | 1 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 4 | 4 | 8
| Meston | Lower Ground | Room 082 | AC shuttering between double roof support beam | 20 | Chrysotile | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 4 | 4 | 8
| Meston | Lower Ground | Room 082 | AIB packers to 2no. Concrete window columns | 2 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 4 | 4 | 8
| Meston | Lower Ground | Room 083 (was 077) | Fume cabinet lining | 2 | Chrysotile |  | 4 | 6 | 10
| Meston | Lower Ground | Room 083 (was 077) | Square profile AIB ducting to fume cabinets in ceiling void | 5 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 6 | 3 | 9
| Meston | Lower Ground | Room 083 (was 077) | AIB packers to 1no. Concrete window columns | 1 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 4 | 4 | 8
| Meston | Lower Ground | Room 083 (was 077) | Round profile AC ducting to fume cabinets in ceiling void | 5 | Chrysotile | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 3 | 3 | 6
| Meston | Lower Ground | Room 084 (Was 079) | Suspended ceiling tiles | 8 | Amosite | Popped tiles refitted by Cape 8/2/2010 | 6 | 4 | 10
| Meston | Lower Ground | Room 084 (Was 079) | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 084 (Was 079) | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 084 (Was 079) | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Lower Ground | Room 084 (Was 079) | Heating boxing below windows | 8 | Amosite | Encapsulated by Cape 8/2/2010. Labelled. | 4 | 4 | 8
| Meston | Lower Ground | Room 084 (Was 079) | Window column cladding | 4 | Amosite | Re-painted by Cape 8/2/2010 | 4 | 4 | 8
| Meston | Lower Ground | Room 084 (Was 079) | Low level AIB wall panel adjoining 087 (In heater void) | 1 | Amosite | Revealed during renovation-all items encapsulated as necessary by Rhodar Jan 2009 | 5 | 3 | 8
| Meston | Lower Ground | Room 085 (was 080) WC | Suspended ceiling tiles | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 085 WC | Insulation board boxing | 2 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Room 086 Fluid Mechanics | Pipe insulation in floor duct | 5 | Amosite | Encapsulated where accessible & Labels applied-By Cape Mar 2010 | 6 | 4 | 10
| Meston | Lower Ground | Room 086 Fluid Mechanics | Window column cladding | 20 | Amosite | Encapsulated where accessible & Labels applied-By Cape Mar 2010 | 5 | 4 | 9
| Meston | Lower Ground | Room 086 Fluid Mechanics | Soffit above windows | 30 | Amosite | Encapsulated where accessible & Labels applied-By Cape Mar 2010 | 5 | 4 | 9
| Meston | Lower Ground | Room 086 Fluid Mechanics | Ceiling upstand | 30 | Amosite | Encapsulated where accessible & Labels applied-By Cape Mar 2010 | 5 | 4 | 9
| Meston | Lower Ground | Room 086 Fluid Mechanics | Heating boxing below windows | 30 | Amosite | Encapsulated where accessible & Labels applied-By Cape Mar 2010 | 5 | 4 | 9
| Meston | Lower Ground | Room 086 Fluid Mechanics | Rope seal to ventilation ducting | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | Lower Ground | Room 086 Fluid Mechanics | Small flue pipes | 1 | Chrysotile |  | 4 | 4 | 8
| Meston | Lower Ground | Room 086 Fluid Mechanics | Cement Flue at ceiling | 5 | Chrysotile |  | 4 | 1 | 5
| Meston | Lower Ground | Room 086 Fluid Mechanics-floor duct | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | Lower Ground | Room 087 (was 081) | Heating boxing below windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 087 (was 081) | Soffit above windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 087 (was 081) | Ceiling upstand | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 088 (was 086) Receiving Bay | Suspended ceiling tiles | 12 | Amosite | Ceiling repaired & fully re-painted by Cape March 2010. 2 Rows of tiles removed by cargo door Sept 2014 | 5 | 5 | 10
| Meston | Lower Ground | Room 089 (was 086a) | Soffit above windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 089 (was 086a) | Ceiling upstand | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 089 (Was086a) | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | Lower Ground | Room 090 | Suspended ceiling tiles | 18 | Amosite |  | 6 | 6 | 12
| Meston | Lower Ground | Room 090 | Soffit above windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 090 | Ceiling upstand | 9 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 090 WC | Suspended ceiling tiles | 4 | Amosite |  | 6 | 4 | 10
| Meston | Lower Ground | Room 090 WC | Soffit above windows | 2 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Room 090 WC | Ceiling upstand | 2 | Amosite |  | 6 | 3 | 9
| Meston | Lower Ground | Stairwell B | Pipe going through wall above fire doors | 5 | Amosite | Labelled | 8 | 4 | 12
| Meston | Lower Ground | Stairwell B | Pipe above fire doors to left hand side | 5 | Amosite | Labelled | 8 | 4 | 12
| Meston | Lower Ground | Vending Machine Area ceiling void | Cloth packer to pipe hangers | 1 | chrysotile | Encapsulated by Cape during removal works Aug 2010 | 4 | 5 | 9
| Meston | Lower Ground | Vending Machine Area-window column | AIB packers embedded in concrete | 1 | Amosite | Encapsulated by Cape during removal works Aug 2010 | 5 | 5 | 10
| Meston | Lower Ground | Void between male & female WC | WC cistern on wall | 1 | Amosite |  | 2 | 2 | 4
| Meston | Ground | Ceiling void adj G06a | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | Ground | Cleaners Store | Suspended ceiling tiles | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Cleaners Store | WC cistern on wall | 1 | Amosite |  | 4 | 3 | 7
| Meston | Ground | Corridor 3 | Insulation to pipework | 8 | Amosite | Encapsulated by Cape Aug 2010 | 6 | 4 | 10
| Meston | Ground | Corridor 3 - adj. G17/18 | Insulation to pipes over entrance | 6 | Amosite | Encapsulated by Cape Aug 2010 | 6 | 4 | 10
| Meston | Ground | Corridor 3 - between G19&20 | Insulation to pipework | 5 | Amosite | Encapsulated by Cape Aug 2010 | 6 | 4 | 10
| Meston | Ground | Corridor 3, to left of G33 entrance | Insulation to pipework | 8 | Amosite | Encapsulated by Cape Aug 2010 | 6 | 4 | 10
| Meston | Ground | Corridor 3, to left of G34 entrance | Insulation to pipework | 6 | Amosite | Encapsulated by Cape Aug 2010 | 6 | 4 | 10
| Meston | Ground | Corridor 3, to right of G32 entrance | Insulation to pipework | 4 | Amosite | Encapsulated by Cape Aug 2010 | 6 | 4 | 10
| Meston | Ground | Corridor 6 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Corridor 6 | Insulating board to boxing over fire doors | 2 | Amosite | Repaired by Cape Dec 09 | 6 | 3 | 9
| Meston | Ground | Corridor 6 | Flash guards in electrical boxing | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | Ground | Corridor 7 | Insulating board above fire doors | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Corridor 7 | Insulating board to boxing over fire doors | 2 | Amosite | Repaired by Cape Dec 09 | 6 | 3 | 9
| Meston | Ground | Corridor 7 | Suspended ceiling tiles | 30 | Amosite | Repaired by Cape Dec 09 | 5 | 4 | 9
| Meston | Ground | Corridor 7 | Flash guards in electrical boxing | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | Ground | Corridor 8 | Suspended ceiling tiles | 100 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Corridor 8 | Insulating board above fire doors | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Dark room adj G61 | Suspended ceiling tiles | 8 | Amosite | Painted by Cape Sep 12 | 5 | 5 | 10
| Meston | Ground | Female WC | Suspended ceiling tiles | 12 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Female WC | Soffit above windows | 4 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Female WC | Ceiling upstand | 4 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Female WC | Window column cladding | 4 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Female WC | Bunnie' Sanitary Incinerator | 1 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Male WC | Suspended ceiling tiles | 15 | Amosite | Ceiling tiles re-seated by Cape Sep 12 | 6 | 4 | 10
| Meston | Ground | Male WC | Window column cladding | 4 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Male WC | Soffit above windows | 7 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Male WC | Ceiling upstand | 7 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Male WC | Waste pipe column cladding | 4 | Amosite | Repaired by Cape 7/1/11 | 5 | 3 | 8
| Meston | Ground | Plant room adj G66 | Cement flue pipes | 20 | Amosite |  | 5 | 1 | 6
| Meston | Ground | Plant room adj G66 | Flue bracket packer | 1 | Chrysotile |  | 5 | 0 | 5
| Meston | Ground | Riser behind switch room G66 | Cement flue pipes | 30 | Crocidolite |  | 6 | 1 | 7
| Meston | Ground | Riser outside G05b | Pipe insulation & debris | 5 | Amosite | Riser is padlocked off. | 11 | 1 | 12
| Meston | Ground | Riser outside G17/18 | Pipe insulation & debris | 5 | Crocidolite | Riser is padlocked off. | 12 | 1 | 13
| Meston | Ground | Room G03a | Ventilation ducting cement cladding | 5 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G06 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G06a plant room | Soffit above windows | 4 | Amosite |  | 6 | 2 | 8
| Meston | Ground | Room G06a plant room | Ceiling upstand | 4 | Amosite |  | 6 | 2 | 8
| Meston | Ground | Room G06a plant room | Heating boxing below windows | 4 | Amosite |  | 6 | 2 | 8
| Meston | Ground | Room G07 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G07 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G07 | Heating boxing below windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G07 | Window column cladding | 4 | Amosite | Encapsulated by Cape Oct 2010. Labelled | 5 | 4 | 9
| Meston | Ground | Room G07 | Ceiling upstand | 6 | Amosite | Encapsulated by Cape Oct 2010. Labelled | 5 | 4 | 9
| Meston | Ground | Room G08 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G08 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G08 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G08 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G08 | Heating boxing below windows | 12 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G09 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G09 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G09 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G09 | Ceiling upstand | 12 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G09 | Heating boxing below windows | 12 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G09 Ceiling void | Ventilation | 15 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G10 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G10 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G10 | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G10 | Window column cladding | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G10 Ceiling void | Ventilation | 5 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G11 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G11 | Window column cladding | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G11 Ceiling void | Ventilation | 20 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G012 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G12 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G12 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G12 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G12 | Heating boxing below windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G13 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G13 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G13 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G13 | Heating boxing below windows | 12 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G13 | Window column cladding-behind non-asbestos | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G14 | Insulating board debris to ceiling void | 1 | Amosite |  | 8 | 3 | 11
| Meston | Ground | Room G14 | Window column cladding | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G14 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G14 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G15 | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | Ground | Room G16/16a (This is one room) | Cloth packer to pipe hangers | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | Ground | Room G19 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G20 | Oven lining | 1 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G32 | Cement cladding to ventilation ducting | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G33 | Cement cladding to ventilation ducting | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G53 | Suspended ceiling tiles | 14 | Amosite | Ceiling repaired by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G54 | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G55 | Suspended ceiling tiles | 8 | Amosite | Painted by Cape Sep 12 | 5 | 5 | 10
| Meston | Ground | Room G56 | Suspended ceiling tiles | 22 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G56 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G56 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G56 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G56 | Heating boxing below windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G56 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Ground | Room G56 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G57 | Suspended ceiling tiles | 22 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G57 | Fume cabinet lining to bottom storage | 2 | Amosite | Encapsulated by Cape Nov 09 | 6 | 5 | 11
| Meston | Ground | Room G57 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G57 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G57 | Heating boxing below windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G57 | Window column cladding | 4 | Amosite | Encapsulated by Cape Sep 10 | 5 | 4 | 9
| Meston | Ground | Room G57 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G58 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G58 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G58 | Soffit above windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G58 | Ceiling upstand | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G58 | Heating boxing below windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G58 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Ground | Room G58 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G59 | Suspended ceiling tiles | 30 | Amosite | Repaired by Cape May 12 | 6 | 6 | 12
| Meston | Ground | Room G59 | Fume cabinet lining to bottom storage | 2 | Amosite | Encapsulated by Cape Nov 09 | 6 | 5 | 11
| Meston | Ground | Room G59 | Soffit above windows | 14 | Amosite | Enclosed by Cape May 12 | 6 | 4 | 10
| Meston | Ground | Room G59 | Ceiling upstand | 14 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G59 | Heating boxing below windows | 14 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G59 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G59 | Pipe insulation under bench opposite Fume cabinet A | 1 | Amosite | Encapsulated by Cape Dec 2012 | 6 | 5 | 11
| Meston | Ground | Room G60 | Suspended ceiling tiles | 12 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G60 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G61 | Suspended ceiling tiles | 12 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G61 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G62 | Suspended ceiling tiles | 40 | Amosite | Repaired by Cape May 12 | 6 | 7 | 13
| Meston | Ground | Room G62 | Soffit above windows | 12 | Amosite | Enclosed by Cape May 12 | 6 | 5 | 11
| Meston | Ground | Room G62 | Ceiling upstand | 10 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G62 | Heating boxing below windows | 10 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G62 | Window column cladding | 12 | Amosite | Encapsulated by Cape Nov 09 | 5 | 5 | 10
| Meston | Ground | Room G62 | Fume cabinet lining to bottom storage | 2 | Amosite |  | 5 | 5 | 10
| Meston | Ground | Room G62 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Ground | Room G62 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G62 | Loose cement boards on work benches | 1 | Chrysotile |  | 4 | 5 | 9 | Monitor
| Meston | Ground | Room G62 | Pipe insulation under island bench | 1 | Amosite | Encapsulated by Cape May 12 | 7 | 5 | 12
| Meston | Ground | Room G62 | Pipe insulation under bench to fume cabinet adj G69 | 1 | Amosite | Encapsulated by Cape May 12 | 7 | 5 | 12
| Meston | Ground | Room G63 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G66 | Suspended ceiling tiles | 12 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G66 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | Ground | Room G66 electrical store | Suspended ceiling tiles | 4 | Amosite | Encapsulated by Cape 1/7/2009 | 6 | 2 | 8
| Meston | Ground | Room G67 | Suspended ceiling tiles | 15 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G67 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | Ground | Room G68 | Suspended ceiling tiles | 30 | Amosite | Repaired by Cape Sep 12 | 5 | 6 | 11 | Monitor
| Meston | Ground | Room G68 | Ceiling upstand | 15 | Amosite |  | 6 | 4 | 10 | Monitor
| Meston | Ground | Room G68 | Column cladding | 4 | Amosite | Encapsulated by Cape 1/11/08 | 5 | 5 | 10 | Monitor
| Meston | Ground | Room G68 | Pipe insulation adj floor behind work benches | 5 | Amosite | Encapsulated by Cape 1/11/08 | 6 | 4 | 10 | Monitor
| Meston | Ground | Room G68 | Heating boxing below windows | 15 | Amosite | Encapsulated by Cape 1/11/08 | 5 | 5 | 10 | Monitor
| Meston | Ground | Room G68 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Ground | Room G68 | Soffit above windows | 15 | Amosite | Overclad by Cape with timber 8/11/08 | 6 | 4 | 10 | Monitor
| Meston | Ground | Room G68 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G69 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G69 | Window column cladding | 4 | Amosite | Repainted by Cape June 2011 | 4 | 4 | 8
| Meston | Ground | Room G69 | Soffit above windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G69 | Ceiling upstand | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G69 | Heating boxing below windows | 10 | Amosite | Encapsulated by Cape June 2011 | 4 | 4 | 8
| Meston | Ground | Room G69 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G70 | Suspended ceiling tiles | 18 | Amosite | Ceiling repaired by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G70 | Soffit above windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G70 | Ceiling upstand | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G70 | Heating boxing below windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G70 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G71 | Suspended ceiling tiles | 14 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G71 | Window column cladding | 7 | Amosite | Column clad by Cape Sep 12 | 5 | 4 | 9
| Meston | Ground | Room G71 | Soffit above windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G71 | Ceiling upstand | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G71 | Heating boxing below windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G71 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G72 | Suspended ceiling tiles | 14 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G72 | Soffit above windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G72 | Ceiling upstand | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G72 | Heating boxing below windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G73 | Suspended ceiling tiles | 12 | Amosite | Minor repairs by Cape Sep 12 | 5 | 5 | 10
| Meston | Ground | Room G73 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G73 | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G73 | Heating boxing below windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G74 | Suspended ceiling tiles | 18 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G74 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G74 | Soffit above windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G74 | Ceiling upstand | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G74 | Heating boxing below windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G74 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G76 | Suspended ceiling tiles | 20 | Amosite | Repaired by Cape Dec 09/Further minor repairs by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G77 | Suspended ceiling tiles | 8 | Amosite | Repainted by Cape Sep 12 | 5 | 5 | 10
| Meston | Ground | Room G78 | Suspended ceiling tiles | 12 | Amosite | Repaired by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G78 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Ground | Room G78 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G78 | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G78 | Heating boxing below windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G78 | Window column cladding | 4 | Amosite | Lower half clad by Cape Sep 12 | 5 | 4 | 9
| Meston | Ground | Room G78 | Equipment' cement panels | 1 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G79 | Suspended ceiling tiles | 15 | Amosite | Ceiling repaired by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G79 | Ceiling upstand | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G79 | Soffit above windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G79A | Heating boxing below windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G79B | Heating boxing below windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G82 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G82 | Ceiling upstand | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G82 | Soffit above windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G82 | Heating boxing below windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G82 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G85 | Suspended ceiling tiles | 16 | Amosite | Minor repairs by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G85 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G85 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G85 | Heating boxing below windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G89 | Suspended ceiling tiles | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G90 | Ceiling panels | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G90 | Wall panels | 10 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G91 | Ducting in ceiling void | 3 | Amosite | Encapsulated by Rhodar April 16 | 4 | 1 | 5
| Meston | Ground | Room G91 | Pipe bracket pad | 5 | Chrysotile | Encapsulated by Rhodar April 16 | 3 | 1 | 4
| Meston | Ground | Room G92 Japp Lab | Fume cabinet lining | 2 | Chrysotile | 6 fume cabinets | 5 | 5 | 10
| Meston | Ground | Room G92 Japp Lab | Window column cladding | 4 | Amosite | Encapsulated by Cape Sep 2010 | 5 | 4 | 9
| Meston | Ground | Room G92 Japp Lab | Heating boxing below windows | 20 | Amosite | Encapsulated by Cape Sep 2010 | 5 | 4 | 9
| Meston | Ground | Room G92 Japp Lab | Soffit above windows | 20 | Amosite | Encapsulated by Cape Sep 2010/Overclad by Cape Sep 12 | 5 | 4 | 9
| Meston | Ground | Room G92 Japp Lab | Ceiling upstand | 20 | Amosite | Encapsulated by Cape Sep 2010 | 5 | 4 | 9
| Meston | Ground | Room G92 Japp Lab | Ducting in ceiling void | 30 | Amosite | Encapsulated by Rhodar April 16 | 4 | 1 | 5
| Meston | Ground | Room G92 Japp Lab | Pipe bracket pad | 50 | Chrysotile | Encapsulated by Rhodar April 16 | 3 | 1 | 4
| Meston | Ground | Room G92B | Soffit above windows | 7 | Amosite | Encapsulated by Cape Sep 2010 | 5 | 4 | 9
| Meston | Ground | Room G92B | Ceiling upstand | 7 | Amosite | Encapsulated by Cape Sep 2010 | 5 | 4 | 9
| Meston | Ground | Room G92B | Heating boxing below windows | 7 | Amosite | Encapsulated by Cape Sep 2010 | 5 | 4 | 9
| Meston | Ground | Room G92B | Ducting in ceiling void | 40 | Amosite | Encapsulated by Rhodar April 16 | 4 | 1 | 5
| Meston | Ground | Room G92B | Pipe bracket pad | 5 | Chrysotile | Encapsulated by Rhodar April 16 | 3 | 1 | 4
| Meston | Ground | Room G92C | Soffit above windows | 9 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G92C | Ceiling upstand | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G92C | Window column cladding | 4 | Amosite | Encapsulated by Cape Sep 2010 | 6 | 4 | 10
| Meston | Ground | Room G92C | Heating boxing below windows | 12 | Amosite | Encapsulated by Cape Sep 2010 | 6 | 4 | 10
| Meston | Ground | Room G92C | Ducting in ceiling void | 3 | Amosite | Encapsulated by Rhodar April 16 | 4 | 1 | 5
| Meston | Ground | Room G92C | Pipe bracket pad | 5 | Chrysotile | Encapsulated by Rhodar April 16 | 3 | 1 | 4
| Meston | Ground | Room G93 | Suspended ceiling tiles | 18 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G93 | Fume cabinet lining | 2 | Chrysotile |  | 6 | 5 | 11
| Meston | Ground | Room G93 | Soffit above windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G93 | Ceiling upstand | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G93 | Heating boxing below windows | 9 | Amosite | Encapsulated by Cape Oct 14 | 6 | 4 | 10
| Meston | Ground | Room G94 | Suspended ceiling tiles | 12 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G94 | Window column cladding | 4 | Amosite | Sep 12-column clad at desk height & painted | 5 | 4 | 9
| Meston | Ground | Room G94 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G94 | Heating boxing below windows | 4 | Amosite | Encapsulated by Cape Oct 14 | 6 | 4 | 10
| Meston | Ground | Room G94 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G95 | Suspended ceiling tiles | 12 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G95 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G95 | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G95 | Heating boxing below windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G95 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | Ground | Room G96 | Suspended ceiling tiles | 14 | Amosite |  | 6 | 5 | 11
| Meston | Ground | Room G96 | Window column cladding | 4 | Amosite | Lower half clad by Cape Sep 12 | 5 | 4 | 9
| Meston | Ground | Room G96 | Soffit above windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G96 | Ceiling upstand | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G96 | Heating boxing below windows | 7 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G99 | Suspended ceiling tiles | 15 | Amosite | Minor repairs by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G99 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G99 | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G99 | Heating boxing below windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G99 Flue riser | Cement flues | 30 | Chrysotile | Encapsulated By Pyeroy Dec 09 | 3 | 3 | 6
| Meston | Ground | Room G101 | Suspended ceiling tiles | 20 | Chrysotile |  | 4 | 6 | 10
| Meston | Ground | Room G101 | Fume cabinet lining | 2 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G101 | Heating boxing below windows | 9 | Amosite | Encapsulated where accessible by Cape Mar 2011 | 5 | 4 | 9
| Meston | Ground | Room G101 | Soffit above windows | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G101 | Ceiling upstand | 9 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G102 | Window column cladding | 4 | Amosite | Encapsulated by Cape Mar 2011 | 5 | 4 | 9
| Meston | Ground | Room G102 | Fume cabinet lining | 2 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G102 | Soffit above windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G102 | Ceiling upstand | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G103 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 6 | 12
| Meston | Ground | Room G103 | Soffit above windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G103 | Ceiling upstand | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G103 | Heating boxing below windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G103 | Window column cladding | 4 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G103 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | Ground | Room G105 | Suspended ceiling tiles | 14 | Amosite | Missing tiles replaced by Cape Sep 12 (non-asbestos replacements) | 6 | 6 | 12
| Meston | Ground | Room G105 | Soffit above windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G105 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G105 | Window column cladding | 4 | Amosite | Repainted by Cape Sep 12 | 5 | 4 | 9
| Meston | Ground | Room G105 | Heating boxing below windows | 8 | Amosite | Encapsulated by Cape Oct 14 | 6 | 4 | 10
| Meston | Ground | Room G105 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | Ground | Room G106 | Suspended ceiling tiles | 14 | Amosite | Minor repairs by Cape Sep 12 | 5 | 6 | 11
| Meston | Ground | Room G106 | Soffit above windows | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G106 | Ceiling upstand | 6 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Room G106 | Heating boxing below windows | 5 | Amosite | Encapsulated by Cape Oct 14 | 6 | 4 | 10
| Meston | Ground | Room G106 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | Ground | Room G106 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | Ground | Stairwell D | Suspended ceiling tiles | 10 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Stairwell D | Insulating board cladding to wall | 5 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Stairwell D | Soffit above windows | 4 | Amosite |  | 6 | 3 | 9
| Meston | Ground | Stairwell E | Electrical boxing - cloth flash guards | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | Ground | Stairwell E | Suspended ceiling tiles | 20 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Stairwell E | Soffit above windows | 11 | Amosite |  | 6 | 4 | 10
| Meston | Ground | Stairwell E | Electrical boxing lining | 4 | Amosite | Encapsulated by Cape Sep 09 | 5 | 4 | 9
| Meston | Ground | Switchroom adj. G89 | Cloth flash guards | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | Ground | Wall void opposite lift adj 076 | Cement flue | 40 | Chrysotile |  | 5 | 4 | 9
| Meston | Ground | WC at room G99 | Suspended ceiling tiles | 4 | Amosite |  | 6 | 5 | 11
| Meston | Between Ground & 1st | Cleaners store riser | Cloth flash guards to electrical box | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | 1st | Cleaners Store | Suspended ceiling tiles | 6 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Cleaners Store | WC cistern | 1 | Amosite |  | 3 | 5 | 8
| Meston | 1st | Cleaners Store at lift | Suspended ceiling tiles | 4 | Amosite | Re-seated by Cape Dec 09 | 5 | 4 | 9
| Meston | 1st | Cleaners Store at lift | WC cistern | 1 | Amosite |  | 3 | 3 | 6
| Meston | 1st | Corridor 6 - Bridge | Suspended ceiling tiles | 40 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Corridor 6 - Bridge | Ceiling upstand | 20 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Corridor 6 - Bridge | Soffit above windows | 20 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Corridor 6 - Bridge | Upstand within ceiling void | 8 | Amosite |  | 7 | 5 | 12
| Meston | 1st | Corridor 7 | Asbestos samples in display cabinet | 1 | Crocidolite | In mineral form | 6 | 2 | 8
| Meston | 1st | Corridor 8 | Electrical boxing above fire doors-cladding | 2 | Amosite | Debris cleaned & board repainted where accessible by Cape 10-1-09 | 5 | 6 | 11
| Meston | 1st | Corridor 8 | Electrical boxing above fire doors-flash guards | 1 | Chrysotile |  | 4 | 6 | 10
| Meston | 1st | Corridor 8 | Suspended ceiling tiles | 15 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Corridor 8 & 9 | Insulation board cladding over fire doors | 6 | Amosite |  | 6 | 3 | 9
| Meston | 1st | Corridor 9 | Suspended ceiling tiles | 9 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Corridor 9 Electrical store | Suspended ceiling tiles | 4 | Amosite |  | 6 | 2 | 8
| Meston | 1st | Corridor 9 Electrical store | Ceiling tile | 1 | Amosite | Cleaned & tiles repaired by Cape Dec 09 | 5 | 2 | 7
| Meston | 1st | Corridor 9 Electrical store | Flash guards | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | 1st | Electrical store across from lift | Flash guards | 1 | Chrysotile |  | 5 | 2 | 7
| Meston | 1st | Female WC | Sanitary Incinerator | 1 | Amosite | Presumed | 5 | 4 | 9
| Meston | 1st | Female WC | Suspended ceiling tiles | 10 | Amosite |  | 5 | 4 | 9
| Meston | 1st | Female WC | Ceiling upstand | 4 | Amosite |  | 5 | 4 | 9
| Meston | 1st | Female WC | Soffit above windows | 2 | Amosite |  | 5 | 4 | 9
| Meston | 1st | Female WC | Window column cladding | 4 | Amosite |  | 5 | 4 | 9
| Meston | 1st | Female WC adj. stairwell | Suspended ceiling tiles | 15 | Amosite | Tiles re-seated by Cape 10-1-09 | 5 | 4 | 9
| Meston | 1st | Female WC adj. stairwell | Heating boxing below windows | 4 | Amosite |  | 5 | 3 | 8
| Meston | 1st | Female WC adj. stairwell | Ceiling upstand | 6 | Amosite |  | 5 | 3 | 8
| Meston | 1st | Female WC adj. stairwell | Soffit above windows | 6 | Amosite |  | 5 | 3 | 8
| Meston | 1st | Fire exit stairwell | Wall panels | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Fire exit stairwell | Nosing strip to stairs | 30 | Chrysotile |  | 2 | 5 | 7
| Meston | 1st | Male WC | Suspended ceiling tiles | 14 | Amosite | Tiles re-seated by Cape 10-1-09 | 5 | 4 | 9
| Meston | 1st | Male WC | Ceiling upstand | 3 | Amosite |  | 5 | 4 | 9
| Meston | 1st | Male WC | Soffit above windows | 3 | Amosite |  | 5 | 4 | 9
| Meston | 1st | Male WC | Window column cladding | 4 | Amosite |  | 5 | 4 | 9
| Meston | 1st | Riser adj Room 166 | Cement flue from 1st to basement | 20 | Chrysotile |  | 4 | 1 | 5
| Meston | 1st | Riser behind electrical store | Cement flue pipes | 20 | Amosite |  | 5 | 1 | 6
| Meston | 1st | Riser in room 155K | Cement flue pipes | 40 | Chrysotile |  | 4 | 2 | 6
| Meston | 1st | Riser outside room 112 | Pipe insulation & debris | 3 | Amosite | Riser locked off | 11 | 3 | 14 | Removal
| Meston | 1st | Riser outside room 131 | Pipe insulation & debris | 5 | Chrysotile & Amosite | Riser locked off | 11 | 2 | 13
| Meston | 1st | Riser outside room 131 | Rope seal to ventilation ducting | 2 | Chrysotile | Riser locked off | 5 | 2 | 7
| Meston | 1st | Riser outside room 131 | Ventilation ducting cement cladding | 4 | Chrysotile | Riser locked off | 4 | 2 | 6
| Meston | 1st | Room 115 | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 4 | 6
| Meston | 1st | Room 118 | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 4 | 6
| Meston | 1st | Room 118 riser cupboard | Rope seal to ventilation ducting | 4 | Chrysotile | Riser locked off | 5 | 2 | 7
| Meston |  | 118 Corridor | Glue under floor tiles/carpet in corridor | 30 | Chrysotile
| Meston | 1st | Room 118 riser cupboard | Ventilation ducting cement cladding | 8 | Chrysotile | Riser locked off | 4 | 2 | 6
| Meston | 1st | Room 119 | Soffit above windows | 2 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 119 | Debris above suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 119 | Window column cladding | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 119a | Debris above suspended ceiling tiles | 8 | Amosite | Access formally restricted to all ceiling voids in Meston | 8 | 5 | 13
| Meston | 1st | Room 119a | Heating boxing below windows | 12 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 119a | Window column cladding | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 119a | Soffit above windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 119b | Debris above suspended ceiling tiles | 8 | Amosite | Access formally restricted to all ceiling voids in Meston | 8 | 5 | 13
| Meston | 1st | Room 119b | Heating boxing below windows | 12 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 119b | Window column cladding | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 119b | Soffit above windows | 2 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 120 | Debris above suspended ceiling tiles | 8 | Amosite | Access formally restricted to all ceiling voids in Meston | 8 | 5 | 13
| Meston | 1st | Room 120 | Heating boxing below windows | 12 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 120 | Window column cladding | 8 | Amosite | Re-painted and part-boarded by Cape Jul 11 | 5 | 5 | 10
| Meston | 1st | Room 120 | Soffit above windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 120 | Ceiling upstand | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 121 | Debris above suspended ceiling tiles | 8 | Amosite | Access formally restricted to all ceiling voids in Meston | 8 | 5 | 13
| Meston | 1st | Room 121 | Heating boxing below windows | 12 | Amosite | Raw, but enclosed | 6 | 6 | 12
| Meston | 1st | Room 121 | Window column cladding | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 121 | Ceiling upstand | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 121 | Soffit above windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 122 | Debris in ceiling void | 10 | Amosite | Access prohibited above all false ceilings | 7 | 6 | 13
| Meston | 1st | Room 122 | Window column cladding | 10 | Amosite | Re-painted and part-boarded by Cape Jul 11 | 5 | 5 | 10
| Meston | 1st | Room 122 | Soffit above windows | 10 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 122 | Heating boxing below windows | 10 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 124 | Heating boxing below windows | 12 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 124 | Window column cladding | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 124 | Ceiling upstand | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 124 | Soffit above windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 124 - electrical cupboard | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 125 | Ceiling upstand | 6 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 125 | Soffit above windows | 4 | Amosite | Overclad by Cape with timber Sep 2011 | 5 | 5 | 10
| Meston | 1st | Room 125 | Heating boxing below windows | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 125 | Soffit above windows | 4 | Amosite | Overclad by Cape with timber Sep 2011 | 5 | 5 | 10
| Meston | 1st | Room 125 WC | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 126 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 126 | Heating boxing below windows | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 126 | Ceiling upstand | 6 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 126 | Soffit above windows | 4 | Amosite | Overclad by Cape with timber Sep 2011 | 5 | 5 | 10
| Meston | 1st | Room 127 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 127 | Heating boxing below windows | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 127 | Ceiling upstand | 6 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 127 | Soffit above windows | 4 | Amosite | Overclad by Cape with timber Sep 2011 | 5 | 5 | 10
| Meston | 1st | Room 128 | Suspended ceiling tiles | 20 | Amosite | Patched by Cape Sep 2011 | 5 | 6 | 11
| Meston | 1st | Room 128 | Heating boxing below windows | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 128 | Ceiling upstand | 6 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 128 | Soffit above windows | 4 | Amosite | Overclad by Cape with timber Sep 2011 | 5 | 5 | 10
| Meston | 1st | Room 144a | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 4 | 6
| Meston | 1st | Room 154 | Suspended ceiling tiles | 20 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 154 | Window column cladding | 4 | Amosite | Encapsulated by Cape 22/11/08 | 6 | 5 | 11
| Meston | 1st | Room 154 | Ceiling upstand | 11 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 154 | Soffit above windows | 5 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 154 | Heating boxing below windows | 5 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 155 | Heating boxing below windows | 60 | Amosite | Largely inaccessible, painted where visible. | 6 | 6 | 12
| Meston | 1st | Room 155 | Suspended ceiling tiles | 200 | Amosite | Re-painted by decorators Dec 09 | 5 | 6 | 11
| Meston | 1st | Room 155 | Window column cladding | 40 | Amosite | Encapsulated by Cape 22/11/08 | 6 | 5 | 11
| Meston | 1st | Room 155 | Soffit above windows | 40 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155 | Ceiling upstand | 20 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155 | Fume cabinet-under storage lining | 4 | Amosite | Encapsulated by Cape 15/9/10 | 5 | 5 | 10
| Meston | 1st | Room 155 | Fume cabinet lining | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | 1st | Room 155 | Fume cabinet lining | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | 1st | Room 155 | Flash guards | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | 1st | Room 155 | Wall & ceiling cladding to electrical box | 2 | Amosite | Encapsulated by Cape 22/11/08 | 5 | 2 | 7
| Meston | 1st | Room 155B | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155B | Window column cladding | 4 | Amosite | Encapsulated by Cape 22/11/08 | 6 | 5 | 11
| Meston | 1st | Room 155B | Heating boxing below windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155C | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155C | Heating boxing below windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155D | Tile debris in ceiling void | 1 | Amosite | Void sealed by Cape 22/11/08 | 9 | 5 | 14 | Material cannot be removed without full ceiling removal.
| Meston | 1st | Room 155D | Heating boxing below windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155D | Top oven rope door seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | 1st | Room 155D | Blue kiln | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | 1st | Room 155D | Top oven internal lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | 1st | Room 155D | Bottom oven internal lining | 2 | Chrysotile |  | 4 | 5 | 9
| Meston | 1st | Room 155E | Tile debris in ceiling void | 1 | Amosite | Void sealed by Cape 22/11/08 | 9 | 5 | 14 | Material cannot be removed without full ceiling removal.
| Meston | 1st | Room 155E | Heating boxing below windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155F | Tile debris in ceiling void | 1 | Amosite | Void sealed by Cape 22/11/08 | 9 | 5 | 14 | Material cannot be removed without full ceiling removal.
| Meston | 1st | Room 155F | Suspended ceiling tiles | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155G | Soffit above windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155G | Ceiling upstand | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155G | Window column cladding | 4 | Amosite | Encapsulated by Cape 22/11/08 | 6 | 5 | 11
| Meston | 1st | Room 155G | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155H | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155H | Soffit above windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155H | Ceiling upstand | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155H | Heating boxing below windows | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155J | Suspended ceiling tiles | 30 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155J | Window column cladding | 6 | Amosite | Encapsulated by Cape 13/12/08 | 6 | 5 | 11
| Meston | 1st | Room 155J | Soffit above windows | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155J | Ceiling upstand | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155J | Heating boxing below windows | 12 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 155K | Suspended ceiling tiles | 20 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 155K | Fume cabinet lining | 2 | Chrysotile |  | 4 | 3 | 7
| Meston | 1st | Room 156 | Suspended ceiling tiles | 200 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 156 | Heating boxing below windows | 55 | Amosite | Inaccessible | 6 | 6 | 12
| Meston | 1st | Room 156 | Soffit above windows | 40 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 156 | Ceiling upstand | 15 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 156 | Window column cladding | 12 | Amosite | Encapsulated by Cape 13/12/08 | 6 | 5 | 11
| Meston | 1st | Room 156 | Gallenkamp hotplates | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | 1st | Room 156 | Gallenkamp oven seal | 1 | Chrysotile |  | 5 | 5 | 10
| Meston | 1st | Room 156 | Fume cabinet lining | 2 | Amosite |  | 4 | 5 | 9
| Meston | 1st | Room 156a | Suspended ceiling tiles | 10 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 156b | Suspended ceiling tiles | 10 | Amosite |  | 6 | 6 | 12
| Meston | 1st | Room 157 | Suspended ceiling tiles | 8 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 157 | Soffit above windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 157 | Ceiling upstand | 4 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 157 | Heating boxing below windows | 4 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 158 | Soffit above windows | 10 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 158 | Ceiling upstand | 8 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 158 | Heating boxing below windows | 8 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 159 | Heating boxing below windows | 15 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 165 | Flue ducting below cabinet benches | 15 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 165 | Window column cladding | 12 | Amosite | All re-painted by Cape 10-1-09 | 5 | 6 | 11
| Meston | 1st | Room 165 | Ceiling upstand | 10 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 165 | Heating boxing below windows | 20 | Amosite | Debris cleaned & repainted where accessible by Cape 10-1-09. Further painting carried out Dec 12 | 6 | 5 | 11
| Meston | 1st | Room 165 | Suspended ceiling tiles | 80 | Amosite | Minor painting & re-seating by Cape - 10-1-09. Re-painted by decorators Dec 09 | 5 | 5 | 10
| Meston | 1st | Room 165 | Soffit above windows | 12 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Room 165 | Carbolite oven-outer cladding | 5 | Chrysotile |  | 4 | 5 | 9
| Meston | 1st | Room 165 | Fume cabinet lining | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | 1st | Room 165 | Work bench Housing lining | 25 | Amosite | Presumed | 6 | 7 | 13
| Meston | 1st | Room 165 | Gallenkamp hotplates | 1 | Chrysotile |  | 4 | 4 | 8
| Meston | 1st | Room 165 Store | Suspended ceiling tiles | 4 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 165b | Suspended ceiling tiles | 14 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 165c | Suspended ceiling tiles | 12 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 165c | Ceiling upstand | 6 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 165c | Soffit above windows | 6 | Amosite |  | 6 | 5 | 11
| Meston | 1st | Room 165c | Heating boxing below windows | 6 | Amosite | Debris cleaned & repainted where accessible by Cape 10-1-09 | 6 | 5 | 11
| Meston | 1st | Room 166 | Suspended ceiling tiles | 15 | Amosite | Minor painting & re-seating by Cape - 10-1-09 | 5 | 5 | 10
| Meston | 1st | Stairwell | Suspended ceiling tiles | 12 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Stairwell | Combined soffit & upstand to ceiling | 6 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Stairwell D | Suspended ceiling tiles | 20 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Stairwell D | Insulation board cladding to walls | 9 | Amosite |  | 6 | 3 | 9
| Meston | 1st | Stairwell D | Ceiling upstand | 4 | Amosite |  | 6 | 3 | 9
| Meston | 1st | Stairwell D | Soffit above windows | 4 | Amosite |  | 6 | 3 | 9
| Meston | 1st | Stairwell D | Stair nosing strips | 30 | Amosite |  | 2 | 3 | 5
| Meston | 1st | Stairwell E | Suspended ceiling tiles | 30 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Stairwell E | Panels below windows | 40 | Amosite |  | 6 | 4 | 10
| Meston | 1st | Stairwell E | Soffit above windows | 4 | Amosite |  | 6 | 3 | 9
| Meston | 1st | Stairwell E | Ceiling upstand | 5 | Amosite |  | 6 | 3 | 9
| Meston | 1st | Stairwell E | Stair nosing strips | 30 | Chrysotile |  | 2 | 3 | 5
| Meston | Between 1st & 2nd | Cleaners store riser | Cloth flash guards to electrical box | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | 2nd | East fire exit corridor riser | Rope seal to ventilation ducting | 2 | Chrysotile | Riser locked off | 5 | 3 | 8
| Meston | 2nd | East fire exit corridor riser | Ventilation ducting cement cladding | 4 | Chrysotile | Riser locked off | 4 | 3 | 7
| Meston | 2nd | Riser in corridor 2/3 | Cement debris to floor | 1 | Chrysotile | Riser locked off | 5 | 3 | 8
| Meston | 2nd | Riser outside 216 | Thermal insulation to pipe | 6 | Amosite | Riser locked off | 11 | 4 | 15
| Meston | 2nd | Riser outside 216 | Pipe insulation & debris | 2 | Amosite | Riser locked off | 11 | 4 | 15
| Meston | 2nd | Riser outside 216 | Door and riser framework - debris | 1 | Amosite | Riser locked off | 11 | 4 | 15
| Meston | 2nd | Riser outside 216 | Rope seal to ventilation ducting | 3 | Chrysotile | Riser locked off | 5 | 4 | 9
| Meston | 2nd | Riser outside 216 | Ventilation ducting cement cladding | 4 | Chrysotile | Riser locked off | 4 | 4 | 8
| Meston | 2nd | Riser outside room 233 | Pipe insulation & debris | 3 | Amosite | Riser locked off | 11 | 3 | 14
| Meston | 2nd | Room 217 | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 4 | 6
| Meston | 2nd | Room 217 riser | Rope seal to ventilation ducting | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | 2nd | Room 217 riser | Ventilation ducting cement cladding | 5 | Chrysotile |  | 4 | 3 | 7
| Meston | 2nd | Room 233 | Bitumen pad under sink | 1 | Chrysotile |  | 2 | 4 | 6
| Meston | Between 2nd & 3rd | Cleaners store riser | Cloth flash guards to electrical box | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | 3rd | Corridor 1 | Ventilation ducting cement cladding | 8 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Corridor 2 Electrical riser | Flash guards | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | 3rd | Corridor 2 Electrical riser | Cement panels | 1 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Corridor 2 Riser | Ventilation ducting cement cladding | 7 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Electrical cupboard outside room 309 | Flash guards | 1 | Chrysotile |  | 5 | 3 | 8
| Meston | 3rd | Motor Room 2 | Ventilation ducting cement cladding | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | 3rd | Riser outside 313 | Pipe insulation & debris | 4 | Chrysotile & Amosite | Presumed- Room is padlocked off | 11 | 6 | 17
| Meston | 3rd | Riser outside 336 | Pipe insulation & debris | 4 | Chrysotile & Amosite | Presumed -Room is padlocked off | 11 | 6 | 17
| Meston | 3rd | Room 302 Right hand eaves | Panel with a circular hole | 1 | Chrysotile | Encapsulated by Cape March 2010 | 5 | 4 | 9
| Meston | 3rd | Room 302 Right hand eaves | Switch box rope flash guards | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | 3rd | Room 304 - duct | Ventilation ducting cement cladding | 20 | Chrysotile | Encapsulated by Cape March 2010 | 4 | 4 | 8
| Meston | 3rd | Room 304 Duct | Ventilation ducting cement cladding | 5 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Room 311 ceiling void | Rope seal to ventilation ducting | 6 | Chrysotile |  | 5 | 3 | 8
| Meston | 3rd | Room 311 ceiling void | Ventilation ducting cement cladding | 12 | Chrysotile |  | 4 | 3 | 7
| Meston | 3rd | Room 316 - Duct | Ventilation ducting cement cladding | 20 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Room 317 Electrical Riser | Electrical switch box - fuse holders | 1 | Chrysotile | Presumed | 5 | 5 | 10
| Meston | 3rd | Room 323 Duct | Ventilation ducting cement cladding | 5 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Room 331 | Bitumen adhesive to floor beneath carpet | 14 | Chrysotile |  | 1 | 5 | 6
| Meston | 3rd | Room 333 | Ventilation ducting cement cladding | 8 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Room 334 | Ventilation ducting cement cladding | 8 | Chrysotile |  | 4 | 4 | 8
| Meston | 3rd | Room 335 Kitchen | Ventilation ducting cement cladding | 8 | Chrysotile |  | 4 | 4 | 8
| Meston | 4th | Attic above Corridor 3 | Rope seal to ventilation ducting | 6 | Chrysotile |  | 5 | 4 | 9
| Meston | 4th | Attic above Corridor 3 | Ventilation ducting cement cladding | 8 |  |  | 4 | 4 | 8
| Meston | 4th | Attic above Corridor 3 | Insulation boards around air con penetration through roof | 2 | Chrysotile |  | 4 | 4 | 8
| Meston | 4th | Attic above Rm 401 | Ventilation ducting cement cladding | >50 | Chrysotile |  | 4 | 4 | 8
| Meston | 4th | Attic above Rm 401 | Ventilation ducting rope seals | >50 | Chrysotile |  | 4 | 4 | 8
| Meston | 4th | Attic above Rm 401 | Insulation boards around air con penetration through roof | 8 | Chrysotile |  | 5 | 3 | 8
| Meston | 4th | Attic above Rm 402 | Ventilation ducting rope seals | >50 | Chrysotile |  | 4 | 4 | 8
| Meston | 4th | Attic above Rm 402 | Insulation boards around air con penetration through roof | 8 | Chrysotile |  | 5 | 3 | 8
| Meston | 4th | Attic above Rm 402 | Ventilation ducting cement cladding | >50 | Chrysotile |  | 4 | 4 | 8
| Meston | 4th | Attic from room 406 to Stairwell A | Rope seal to ventilation ducting | 10 | Chrysotile |  | 5 | 5 | 10
| Meston | 4th | Attic from room 406 to Stairwell A | Ventilation ducting cement cladding | >50 | Chrysotile |  | 4 | 5 | 9
| Meston | 4th | Attic from room 406 to Stairwell A | Insulation boards around air con penetration through roof | 8 | Chrysotile |  | 5 | 4 | 9
| Meston | 4th | Room 402a (eaves plantroom) | Ventilation ducting, insulation board boxing | 4 | Chrysotile | Encapsulated by Cape Dec 2009 | 3 | 3 | 6
| Meston | 4th | Room 402a (eaves plantroom) | Ventilation ducting cement cladding | 8 | Chrysotile | Encapsulated by Cape Dec 2009 | 2 | 3 | 5
| Meston | 4th | Room 402b | Rope seal to ventilation ducting | 12 | Chrysotile | Encapsulated by Cape Dec 2009 | 3 | 4 | 7
| Meston | 4th | Room 402b | Ventilation ducting, insulation board boxing | 8 | Chrysotile | Encapsulated by Cape Dec 2009 | 3 | 3 | 6
| Meston | 4th | Room 402b | Electrical fuse box cloth flashguards | 1 | Chrysotile |  | 3 | 3 | 6
| Meston | 4th | Room 402b | Ventilation ducting cement cladding | 8 | Chrysotile | Encapsulated by Cape Dec 2009 | 2 | 3 | 5
| Meston | 4th | Room 402b | Electrical fuse box cement panels | 1 | Chrysotile |  | 2 | 3 | 5
| Meston | 4th | Room 403 | Rope seal to ventilation ducting | 2 | Chrysotile | Encapsulated by Cape 2009 | 3 | 3 | 6
| Meston | 4th | Room 403 | Ventilation ducting cement cladding | 6 | Chrysotile | Encapsulated by Cape 2009 | 2 | 3 | 5
| Meston | 4th | Room 404 | Rope seal to ventilation ducting | 2 | Chrysotile | Encapsulated by Cape Sep 09 | 4 | 2 | 6
| Meston | 4th | Room 404 | Ceiling & beam cladding | 15 | Chrysotile | Encapsulated by Cape Sep 09 | 3 | 2 | 5
| Meston | 4th | Room 404 | Ventilation ducting cement cladding | 6 | Chrysotile | Encapsulated by Cape Sep 09 | 3 | 2 | 5
| Meston | 4th | Room 405 | Electrical fuse box-flashguards | 1 | Chrysotile | Presumed | 5 | 4 | 9
| Meston | 4th | Room 405 | Electrical fuse box cement panels | 1 | Chrysotile | Presumed | 4 | 4 | 8
| Meston | 4th | Room 406 (Water Tank) | Rope seal to ventilation ducting | 11 | Chrysotile | Encapsulated by Rhodar Nov 09 | 3 | 5 | 8
| Meston | 4th | Room 406 (Water Tank) | Gaskets to pipework | 1 | Chrysotile | Encapsulated by Rhodar Nov 09 | 2 | 5 | 7
| Meston | 4th | Room 406 (Water Tank) | Ceiling level Ventilation ducting cement cladding | 8 | Chrysotile | Encapsulated by Rhodar Nov 09 | 2 | 5 | 7
| Meston | 4th | Room 406 (Water Tank) | Ventilation ducting cement cladding | 18 | Chrysotile | Encapsulated by Rhodar Nov 09 | 2 | 5 | 7
| Meston | 4th | Room 406a | Rope seal to ventilation ducting | 4 | Chrysotile | Encapsulated by Cape Dec 09 | 3 | 5 | 8
| Meston | 4th | Room 406a | Ventilation ducting cement cladding | 8 | Chrysotile | Encapsulated by Cape Dec 09 | 2 | 5 | 7
| Meston | 4th | Room 410 | Rope seal to ventilation ducting | 2 | Chrysotile |  | 5 | 5 | 10
| Meston | 4th | Room 410 | Ventilation ducting cement cladding | 4 | Chrysotile |  | 4 | 5 | 9
| Meston | 4th | Room 413 | Rope seal to ventilation ducting | 4 | Chrysotile | Encapsulated by Cape Dec 09 | 3 | 5 | 8
| Meston | 4th | Room 413 | Ventilation ducting cement cladding | 8 | Chrysotile | Encapsulated by Cape Dec 09 | 2 | 5 | 7
| Meston | 4th | Room 423 | Ceiling & beam cladding | 10 | Chrysotile | Encapsulated by Cape Sep 09 | 3 | 3 | 6
| Meston | 4th | Room 427 | Ventilation ducting cement cladding | 12 | Chrysotile |  | 4 | 5 | 9
| Meston | 4th | Room 427 | Rope seal to ventilation ducting | 6 | Chrysotile |  | 5 | 4 | 9
| Meston | 4th | Room 427 | Electrical fuse box-flashguards | 1 | Chrysotile |  | 5 | 4 | 9
| Meston | 4th | Room 427 | Ventilation ducting, insulation board boxing | 8 | Chrysotile |  | 5 | 4 | 9
| Meston | 4th | Room 427 | Rope seal to AHU ventilation ducting | 4 | Chrysotile |  | 5 | 4 | 9
| Meston | 4th | Room 427 | Electrical fuse box cement panels | 1 | Chrysotile |  | 4 | 4 | 8
| Meston | External | Access to car park (under bridge) | Ceiling & beam cladding | 100 | Amosite | Encapsulated by Cape Aug 2010 | 5 | 2 | 7
| Meston | External | Extension - G, LG & 1st floors | Soffit above windows | 200+ | Amosite | 1st floor level delaminating | 6 | 1 | 7
| Meston | External | Extension roof | No 1 Extractor plant room, external soffit | 10 | Chrysotile |  | 4 | 2 | 6
| Meston | External | Extension roof | No 2 Extractor plant room, external soffit | 10 | Chrysotile |  | 4 | 2 | 6
| Meston | External | Extension roof | No 3 Extractor plant room, external soffit | 10 | Chrysotile |  | 4 | 2 | 6
| Meston | External | Extension roof | No 4 Extractor plant room, external soffit | 10 | Chrysotile |  | 4 | 2 | 6
| Meston | External | Extension roof | No 5 Extractor plant room, external soffit | 10 | Chrysotile |  | 4 | 2 | 6
| Meston | External | Extension roof | No 6 Extractor plant room, external soffit | 10 | Chrysotile |  | 4 | 2 | 6
| Meston | External | Extension roof | No 7 Extractor plant room, external soffit | 10 | Chrysotile |  | 4 | 2 | 6
| Meston | External | Extension roof lift motor room | Wall cladding | 40 | Chrysotile | Room cleaned & Asbestos encapsulated by Rhodar Oct 09 | 3 | 3 | 6
| Meston | External | Extension roof Tank room | Wall cladding | 60 | Chrysotile | Room cleaned & Asbestos encapsulated by Rhodar Oct 09 | 3 | 3 | 6
| Meston | External | Extension roof Tank room | AHU rope seal | 1 | Chrysotile | Room cleaned & Asbestos encapsulated by Rhodar Oct 09 | 3 | 3 | 6
| Meston | External | Extension roof Tank room | Cement flue pipes | 8 | Chrysotile | Room cleaned & Asbestos encapsulated by Rhodar Oct 09 | 3 | 2 | 5
| Meston | External | Old building roofs | Soffits to roof windows | 1 | Chrysotile | Presumed | 4 | 0 | 4
| Meston | External | Receiving Bay 1 | Bitumen felt to canopy roof | 20 | Chrysotile |  | 3 | 3 | 6
| Meston | External | Receiving Bay 2 | Canopy ceiling | 20 | Amosite | Encapsulated by Cape March 2010 | 5 | 4 | 9
| Meston | External | Receiving Bay 2 | Canopy soffit | 10 | Chrysotile |  | 4 | 5 | 9
Updated April 2025

## MRF
No asbestos in this building - built 2002

## NEW KINGS
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| New Kings | Basement | X004 switch room | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
Updated April 2025

## NORTH COURT
| Risk Banding | Range | Inspection Frequency
| High | 17+ | 1 Month or unique lock
All info from ACS survey | Significant | 15-16 | 3 Months
Constructed 1994, No Suspect Materials | Medium | 10-14 | 6 Months
| Low | 1-9 | 12 Months

## OLD BREWERY
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Old Brewery | Ground | X003 cleaners cupboard | Distribution board | 1 | Needs sampled |  | 6 | 2 | 8 | Manage & reinspect
| Old Brewery | Ground | X009 | Distribution board | 1 | Needs sampled |  | 6 | 2 | 8 | Manage & reinspect
| Old Brewery | Ground | X010 | Distribution board | 1 | Needs sampled |  | 6 | 2 | 8 | Manage & reinspect
Updated April 2025

## OLD ROCKING HORSE NURSERY
NO ASBESTOS LOCATED IN RPS SURVEY OCT 2011
|  | Risk Banding | Range | Inspection Frequency
|  | High | 17+ | 1 Month or unique lock
| No asbestos in this building | Significant | 15-16 | 3 Months
|  | Medium | 10-14 | 6 Months
|  | Low | 1-9 | 12 Months

## OLD TOWN HOUSE
No asbestos materials detected in 2009 survey
| Risk Banding | Range | Inspection Frequency
| High | 17+ | 1 Month or unique lock
| Significant | 15-16 | 3 Months
| Medium | 10-14 | 6 Months
| Low | 1-9 | 12 Months

## PEDRI UNIT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Pedri Unit | External | Roof | Soffit | 32m | Chrysotile | Encapsulated by Altrad July 2021 | 4 | 0 | 4 | Manage
| Pedri Unit | External | Roof | Soffit | 16m | Chrysotile | Encapsulated by Altrad July 2021 | 4 | 0 | 4 | Manage
| Pedri - 2024 | External electric cupboards | External | Electrics |  |  | No access - presumed | 4 | 0 | 4
Updated April 2025

## PET CENTRE
No asbestos in this building

## PHYTOTRON
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Phytotron Building 2021 | External | Roof | Cement soffits | 25 | Chrysotile |  | 5 | 0 | 5 | Manage
| Phytotron Building 2021 | Ground | Workshop | Cement door header panel | 5 | Chrysotile |  | 5 | 0 | 5 | Manage
| Phytotron Building 2021 | Ground | Workshop | Cement wall panel behind eletrical unit | 1 | Chrysotile |  | 5 | 0 | 5 | Manage
| Phytotron Building 2021 | Ground | Workshop | Cement walls | 10 | Chrysotile |  | 5 | 0 | 5 | Manage
| Phytotron Building 2021 | Ground | Workshop | Electrics (presumed) | 1 | Crocidolite | Needs tested | 5 | 0 | 5 | Manage
Updated April 2025

## POLWARTH
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Polwarth | Basement | Main plant room | Gaskets to pipe work | 1 | Chrysotile |  | 4 | 0 | 4 | Manage & reinspect
| Polwarth | Basement | B:002 | Lift motor brake shoes | 1 | Chrysotile | Needs sampled | 3 | 2 | 5 | Manage & reinspect
| Polwarth | Ground | South plant room | Gaskets to pipe work | 1 | Chrysotile |  | 4 | 0 | 4 | Manage & reinspect
| Polwarth | Ground | South plant room | Gaskets to pipe work (Beldam Crossley) | 1 | Chrysotile |  | 4 | 0 | 4 | Manage & reinspect
| Polwarth | Ground | South plant room | Cloth packers to pipe hangers | 2 | Chrysotile |  | 4 | 5 | 9 | Manage & reinspect
| Polwarth | Ground | North plant room | Cloth packers to pipe hangers | 2 | Chrysotile |  | 4 | 5 | 9 | Manage & reinspect
| Polwarth | Ground | North plant room | Gaskets to pipe work | 1 | Chrysotile |  | 4 | 0 | 4 | Manage & reinspect
| Polwarth | Ground | 0:004 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:007 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:014 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:018 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:019 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:020 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:021 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:025 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:026 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:028 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | Ground | 0:029 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 2nd | 2:015 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 2nd | 2:049 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:007 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:009 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:010 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:012 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:014 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:017 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:022 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:026 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 3rd | 3:028 | Under sink mat | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
| Polwarth | 5th | Lift motor | Brake shoes | 1 | Chrysotile | Needs sampled | 3 | 3 | 6 | Manage & reinspect
| Polwarth | 5th | Roof tank room | Gaskets to pipe work | 1 | Chrysotile |  | 4 | 0 | 4 | Manage & reinspect
Updated April 2025

## POWIS GATE
| Previous Assessments | [27 empty] | Risk Banding | Range | Inspection Frequency
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2009-05-12 | N/A | 2010-05-01 | Images\2009\powisgatesoffit.jpg | High | 17+ | 1 Month or unique lock
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. No change in condition | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2010-06-22 | 8 | 2011-06-01 | Images\2009\powisgatesoffit.jpg | Significant | 15-16 | 3 Months
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. No change in condition | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2010-07-22 | 8 | 2011-07-01 | Images\2009\powisgatesoffit.jpg | Medium | 10-14 | 6 Months
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. No change in condition | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2011-07-18 | 8 | 2012-07-01 | Images\2009\powisgatesoffit.jpg | Low | 1-9 | 12 Months
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. No change in condition | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2012-07-25 | 8 | 2013-07-01 | Images\2009\powisgatesoffit.jpg
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. No change in condition | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2013-07-16 | 8 | 2014-07-01 | Images\2009\powisgatesoffit.jpg
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. No change in condition | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2015-03-30 | 8 | 2016-03-01 | Images\2009\powisgatesoffit.jpg
External | Ground & First Floors | Soffit boards | Inaccessible, presumed asbestos. No change in condition | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2016-02-10 | 8 | 2017-02-01
|  | Soffit boards | Tested and found to be not asbestos | 2 | 1 | 2 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 2018-02-28

## REGENT
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Regent | Ground | G18 electrical cupboard | Woven textiles | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Regent | Ground | G23 electrical cupboard | Woven textiles | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Regent | First | F02 electrical cupboard | Woven textiles | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| Regent | Roof | Plantroom | Gaskets | 1 | Chrysotile |  | 3 | 4 | 7 | Manage & reinspect
Updated April 2025

## ROWETT
No asbestos in this building - built 2015

## SDRL
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
|  | Lower Basement | Electrical | Distribution boards | 15 | Needs sampled |  | 6 | 2 | 8 | Manage & reinspect
Updated April 2025

## SOUTH HOUSE
No asbestos materials detected in March 2024 survey. Sample report in building files
Updated March 2025

## STAFF HOUSING REGISTER
Building name | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
1 Clarks Lane | Ground | Store | Grey floor tiles | 1 | Chrysotile |  | 3 | 4 | 7 | Manage
2 Clark's Lane | Ground | Hall | Floor tiles | 10m2 | Chrysotile | adhesive only | 2 | 3 | 5 | Manage
2 Clark's Lane | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile | adhesive only | 2 | 3 | 5 | Manage
2 Clark's Lane | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile | adhesive only | 2 | 3 | 5 | Manage
2 Clark's Lane | Ground | Bedroom | Floor tiles | 10m2 | Chrysotile | adhesive only | 2 | 3 | 5 | Manage
2 Clark's Lane | Ground | Bedroom | Floor tiles | 6m2 | Chrysotile | adhesive only | 2 | 3 | 5 | Manage
2 Clark's Lane | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile | adhesive only | 2 | 3 | 5 | Manage
2 Clark's Lane | Ground | Living room | Floor tiles | 25m2 | Chrysotile | adhesive only | 2 | 3 | 5 | Manage
2 Clark's Lane | External | Roof | Soffits | 20m | Chrysotile |  | 4 | 3 | 7 | Manage
3A College Bounds | Ground | Stairwell | Floor tiles | 3m2 | Chrysotile |  | 3 | 7 | 10 | Manage
5A College Bounds | Ground | Hall | Floor tiles | 2m2 | Chrysotile |  | 3 | 5 | 8 | Manage
5A College Bounds | Ground | Living room | Floor tiles | 20m2 | Chrysotile |  | 3 | 5 | 8 | Manage
5A College Bounds | First | Bathroom | Toilet cistern | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
7 College Bounds | Ground | Lobby | Floor tiles | 1.5m2 | Chrysotile |  | 3 | 5 | 8 | Manage
7 College Bounds | Ground | Corridor | Floor tiles | 5m2 | Chrysotile |  | 3 | 5 | 8 | Manage
7 College Bounds | Ground | Living room | Floor tiles | 16m2 | Chrysotile |  | 3 | 6 | 9 | Manage
7 College Bounds | Ground | Kitchen | Floor tiles | 8m2 | Chrysotile |  | 3 | 6 | 9 | Manage
7 College Bounds | Ground | Cupboard | Floor tiles | 3m2 | Chrysotile |  | 3 | 5 | 8 | Manage | IF A PROPERTY IS NOT LISTED HERE, IT HAS BEEN SURVEYED AND NO ASBESTOS HAS BEEN DETECTED OR IT HAS BEEN SOLD OR DEMOLISHED
7 College Bounds | Ground | Cupboard | Floor tiles | 3m2 | Chrysotile |  | 3 | 5 | 8 | Manage
8A College Bounds | Ground | bedroom | Boxing panels | 4m2 | Amosite, Chrysotile |  | 6 | 6 | 12 | Manage
22A College Bounds | Stairs | Electrical Cupboard | Flash Guards | 1 |  |  | 3 | 4 | 7 | Manage
22A College Bounds | Communal corridor | electrics | Flash guards | 3 |  |  | 3 | 4 | 7 | Manage
22A College Bounds | External | Garage | Roof | 15m2 |  |  | 1 | 4 | 5 | Manage
24A College Bounds | External | Shed | Roof panels | 20m2 | Chrysotile |  | 4 | 3 | 7 | Manage
22C College Bounds | External | shed | Corrugated roofing sheets | 8 | Chrysotile |  | 4 | 3 | 7 | Manage
26A College Bounds | External | Shed | Roof Panels | 25m2 | Chrysotile |  | 4 | 3 | 7 | Manage
27 College Bounds | External | Shed | Roof Panels | 2m2 | Chrysotile |  | 4 | 3 | 7 | Manage
15 Don Street | Ground | Entrance | Adhesive to floor | 2m2 | Chrysotile |  | 3 | 4 | 7 | Manage
15 Don Street | Ground | Stairwell | Adhesive to floor | 2m2 | Chrysotile |  | 3 | 4 | 7 | Manage
15 Don Street | Ground | Living room | Adhesive to floor | 20m2 | Chrysotile |  | 3 | 5 | 8 | Manage
15 Don Street | Ground | Kitchen | Adhesive to floor | 8m2 | Chrysotile |  | 3 | 4 | 7 | Manage
15 Don Street | Ground | Cupboard | Adhesive to floor | 2m2 | Chrysotile |  | 3 | 4 | 7 | Manage
15 Don Street | Ground | Cupboard | Adhesive to floor | 2m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | Ground | Entrance | Floor tiles | 2m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | Ground | Living room | Floor tiles | 15m2 | Chrysotile |  | 3 | 5 | 8 | Manage
17 Don Street | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | Ground | Kitchen | Floor tiles | 10m2 | Chrysotile |  | 3 | 5 | 8 | Manage
17 Don Street | Ground | Cupboard | Floor tiles | 1.5m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | Ground | Cupboard | Floor tiles | 1.5m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | Ground | lobby | Floor tiles | 2m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | Ground | Bedroom | Floor tiles | 16m2 | Chrysotile |  | 3 | 5 | 8 | Manage
17 Don Street | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile |  | 3 | 4 | 7 | Manage
17 Don Street | External | Shed | Roof Panels | 10m2 | Chrysotile |  | 4 | 4 | 8 | Manage
19 Don St | Ground | Hall | Floor tiles | 8m2 | Chrysotile |  | 3 | 4 | 7 | Manage | IF A PROPERTY IS NOT LISTED HERE, IT HAS BEEN SURVEYED AND NO ASBESTOS HAS BEEN DETECTED OR IT HAS BEEN SOLD OR DEMOLISHED
19 Don St | External | Store | Roof Panels | 30m2 | Chrysotile |  | 3 | 6 | 9 | Manage
25 Don St | Ground | Kitchen | Adhesive to floor | 4m2 | Chrysotile |  | 3 | 4 | 7 | Manage
81 Don St | External | Shed | Shed Panels | 50m2 | Presumed |  | 5 | 4 | 9 | Manage
120 Don St | Ground | Entrance | Adhesive to floor | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
120 Don St | Ground | Living room | Adhesive to floor | 16m2 | Chrysotile |  | 3 | 5 | 8 | Manage
120 Don St | Ground | hall | Adhesive to floor | 4m2 | Chrysotile |  | 3 | 6 | 9 | Manage
120 Don St | ground | Bedroom | Adhesive to floor | 14m2 | Chrysotile |  | 3 | 5 | 8 | Manage
120 Don St | External | Shed | Roof panels | 8m2 | Presumed |  | 6 | 3 | 9 | Manage
124 Don St | External | Shed | Roof panels | 20m2 | Presumed |  | 6 | 3 | 9 | Manage
124 Don St | External | Roof | Flue Cowl | 1m2 | Presumed |  | 5 | 0 | 5 | Manage
124 Don St | First | Loft | Flue pipe | 2m | Presumed |  | 5 | 5 | 10 | Manage
126A Don St | External | Bin Shed | Roof panels | 4m2 | Chrysotile |  | 4 | 3 | 7 | Manage
126B Don St | External | Bin Shed | Roof panels | 3m2 | Chrysotile |  | 4 | 3 | 7 | Manage
1 Eastside Gardens | External | Garage | Roof Panels | 20m2 | Presumed |  | 6 | 3 | 9 | Manage
2 Eastside Gardens | External | Garage | Roof Panels | 10m2 | Chrysotile |  | 3 | 1 | 4 | Manage
3 Eastside Gardens | Ground | Living room | Ceiling textured coating | 20m2 | Chrysotile |  | 3 | 5 | 8 | Manage
4 Eastside Gardens | External | Garage | Roof Panels | 50m2 | Presumed |  | 6 | 3 | 9 | Manage
4 Eastside Gardens | External | Roof | Undercloak | 20m | Chrysotile |  | 5 | 1 | 6 | Manage
6 Eastside Gardens | External | Roof | Undercloak | 20m | Amosite, Chrysotile |  | 6 | 1 | 7 | Manage
8 Eastside Gardens | External | Roof | Undercloak | 20m | Amosite, Chrysotile |  | 6 | 1 | 7 | Manage
9 Eastside Gardens | Ground | Kitchen | sink pad | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
9 Eastside Gardens | External | Roof | Undercloak | 20m | Amosite, Chrysotile |  | 6 | 1 | 7 | Manage
11 Eastside Gardens | External | Roof | Undercloak | 20m | Chrysotile |  | 5 | 1 | 6 | Manage
12 Eastside Gardens | External | Roof | Undercloak | 20m | Chrysotile |  | 5 | 1 | 6 | Manage
13 Eastside Gardens | External | Roof | Undercloak | 20m | Chrysotile |  | 5 | 1 | 6 | Manage
13 Eastside Gardens | Ground | Kitchen | Sink Pad | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
32 Elphinstone Road | External | roof | Two cement cowls | 3 |  | PRESUMED: This material should be tested before being worked upon. | 4 | 1 | 5 | Manage
32 Elphinstone Road | Ground | under stairs, meter cupboard | Bitumen cable wrap | 1 |  | PRESUMED: This material should be tested before being worked upon. | 2 | 2 | 4 | Manage
32 Elphinstone Road | External | shed | Corrugated roofing sheets | 4 | Chrysotile |  | 4 | 3 | 7 | Manage
34 Elphinstone Road | External | Shed | Roof Panels | 4m2 | Chrysotile |  | 4 | 3 | 7 | Manage
2 Firhill Place | External | Roof front & rear | Fascia panel | 6 |  | PRESUMED: This material should be tested before being worked upon. | 6 | 1 | 7 | Manage
2 Grants Place | Ground | Kitchen | Under-sink pad | 1 | Chrysotile |  | 2 | 5 | 7 | Manage
132 Greenburn Rd | External | Garage | Roof panels | 10m2 | Chrysotile |  | 3 | 6 | 9 | Manage
134 Greenburn Rd | External | Garage | Roof panels | 10m2 | Chrysotile |  | 3 | 6 | 9 | Manage
134 Greenburn Rd | First | Loft | Loose lying panel | 1m2 | Chrysotile |  | 4 | 4 | 8 | Remove
136 Greenburn Rd | ground | Kitchen | Sink Pad | 1m2 | Chrysotile |  | 2 | 5 | 7 | Manage
136 Greenburn Rd | External | Garage | Roof panels | 10m2 | Chrysotile |  | 3 | 6 | 9 | Manage
15 High St | Ground | Electrical cupboard | Flash guards & fuse lining | 1m2 | Chrysotile | Information taken from R&D report | 5 | 1 | 6 | Manage
15 High St | Ground | Toilet | Cistern | 1m2 | Amosite | Information taken from R&D report | 3 | 1 | 4 | Manage
15 High St | Ground | Kitchen | Flue | 2m | Presumed Chrysotile | Not included in R&D report | 2 | 1 | 3 | Manage
15 High St | First floor | Stair landing | Flash guards & fuse lining | 1m | Chrysotile | Information taken from R&D report | 5 | 1 | 6 | Manage
33 High Street | Ground | Ground floor rear lobby | Grey floor tiles | 4 | Chrysotile |  | 3 | 4 | 7 | Manage
43 High St | Ground | Kitchen | Sink Pad | 1m2 | Chrysotile |  | 1 | 4 | 5 | Manage
43 High St | External | Out building | Roof Panels | 5m2 | Chrysotile |  | 4 | 3 | 7 | Manage
99 High St | Ground | Office | Safe | 5m2 | Presumed |  | 7 | 5 | 12 | Manage
102 High St | Ground | Hall | Textured coating to ceiling | 4m2 | Chrysotile |  | 4 | 6 | 10 | Manage | IF A PROPERTY IS NOT LISTED HERE, IT HAS BEEN SURVEYED AND NO ASBESTOS HAS BEEN DETECTED OR IT HAS BEEN SOLD OR DEMOLISHED
102 High St | Ground | Corridor | Textured coating to ceiling | 10m2 | Chrysotile |  | 3 | 6 | 9 | Manage
102 High St | First | Stair landing | Textured coating to ceiling | 6m2 | Chrysotile |  | 2 | 6 | 8 | Manage
108 High St | External | Outbuilding | Roof panels | 16m2 | Chrysotile |  | 4 | 3 | 7 | Manage
593 King St | First | Utility Room | Sink pad | 1m2 | Chrysotile |  | 2 | 5 | 7 | Manage
57 Orchard St - entire building | Fourth | Loft | Flue pipes | 4m | Chrysotile |  | 5 | 4 | 9 | Manage
17 St Machar Drive | Ground | Dining Room | paper backed lino | 10m2 | Chrysotile |  | 3 | 7 | 10 | Manage
2 Thom's Court | Ground | Hall | Ceiling textured coating | 2m2 | Chrysotile |  | 3 | 7 | 10 | Manage
2 Thom's Court | Ground | Kitchen | Ceiling textured coating | 6m2 | Chrysotile |  | 3 | 7 | 10 | Manage
4 Thoms Place | Ground | Cupboard | Grey floor tiles | 1 | Chrysotile |  | 3 | 4 | 7 | Manage
4 Thoms Place | Ground | Within meter cupboard | Grey floor tiles | 1 | Chrysotile |  | 3 | 4 | 7 | Manage
54 Tillydrone Ave | Ground | Hall | Floor tiles | 5m2 | Chrysotile |  | 3 | 4 | 7 | Manage
54 Tillydrone Ave | Ground | Dining Room | Floor tiles | 12m2 | Chrysotile |  | 3 | 4 | 7 | Manage
54 Tillydrone Ave | External | Shed | Roof Panels | 40m2 | Chrysotile |  | 4 | 3 | 7 | Manage
54 Tillydrone Ave | Second | Loft | Flue Pipe | 8m2 | Presumed |  | 6 | 2 | 8 | Manage
56 Tillydrone Ave | External | Shed | Roof Panels | 40m2 | Chrysotile |  | 3 | 4 | 7 | Manage
56 Tillydrone Ave | External | Loft | Flue Pipe | 8m | Presumed |  | 6 | 2 | 8 | Manage
56 Tillydrone Ave | Second | Roof | Flue pipe and Cowl | 4m | Presumed |  | 6 | 0 | 6 | Manage
58 Tillydrone Avenue | External | shed | Corrugated roofing sheets | 12 | Chrysotile |  | 4 | 3 | 7 | Manage
60 Tillydrone Ave | External | Shed | Roof Panels | 40m2 | Chrysotile |  | 3 | 4 | 7 | Manage
60 Tillydrone Ave | External | Roof | Flue pipe and Cowl | 4m | Presumed |  | 6 | 0 | 6 | Manage
60 Tillydrone Ave | Second | Loft | Flue pipe | 4m | Presumed |  | 6 | 2 | 8 | Manage
62 Tillydrone Ave | External | Shed | Roof Panels | 40m2 | Chrysotile |  | 3 | 4 | 7 | Manage
62 Tillydrone Ave | External | Roof | Flue pipe and Cowl | 4m | Presumed |  | 6 | 0 | 6 | Manage
62 Tillydrone Ave | Second | Loft | Flue pipe | 4m | Presumed |  | 6 | 2 | 8 | Manage
64 Tillydrone Ave | External | Shed | Shed roof, walls & internal panels | 40m2 | Chrysotile |  | 5 | 4 | 9 | Manage
64 Tillydrone Ave | Second | Loft | Flue pipe x 2 | 8m | Presumed |  | 5 | 2 | 7 | Manage | IF A PROPERTY IS NOT LISTED HERE, IT HAS BEEN SURVEYED AND NO ASBESTOS HAS BEEN DETECTED OR IT HAS BEEN SOLD OR DEMOLISHED
64 Tillydrone Ave | External | Roof | Flue pipe and Cowl x3 | 4m | Presumed |  | 6 | 0 | 6 | Manage
64 Tillydrone Ave | External | Wall | Waste Flange | <1m2 | Presumed |  | 6 | 0 | 6 | Manage
68 Tillydrone Ave | External | Garage | Roof Panels | 30m2 | Presumed |  | 6 | 4 | 10 | Manage
72 Tillydrone Ave | External | Shed | Roof Panels | 20m | Presumed |  | 5 | 4 | 9 | Manage
74 Tillydrone Ave | External | Shed | Shed Panels | 20m2 | Presumed |  | 5 | 4 | 9 | Manage
74 Tillydrone Ave | External | Roof | Flue | 1m | Presumed |  | 6 | 0 | 6 | Manage
76 Tillydrone Avenue | External | shed | Corrugated roofing sheets | 8 | Chrysotile |  | 4 | 3 | 7 | Manage
76 Tillydrone Avenue | Ground | hall & stairs | Brown floor tiles under carpet | 12 | Chrysotile |  | 3 | 4 | 7 | Manage
76 Tillydrone Avenue | Ground | dining room | Brown floor tiles under carpet | 12 | Chrysotile |  | 3 | 4 | 7 | Manage
76 Tillydrone Avenue | Ground | living room | Brown floor tiles under carpet | 12 | Chrysotile |  | 3 | 4 | 7 | Manage
78 Tilldrone Ave | Ground | Hall | Floor tiles | 6m2 | Chrysotile |  | 3 | 5 | 8 | Manage
78 Tilldrone Ave | Ground | Kitchen | Adhesive to floor | 5m2 | Chrysotile |  | 3 | 5 | 8 | Manage
78 Tilldrone Ave | Ground | Cupboard | Adhesive to floor | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
78 Tilldrone Ave | Ground | Dining Room | Floor tiles | 12m2 | Chrysotile |  | 3 | 5 | 8 | Manage
78 Tilldrone Ave | Ground | Living room | Floor tiles | 20m2 | Chrysotile |  | 3 | 5 | 8 | Manage
78 Tilldrone Ave | External | Shed | Shed Panels | 20m2 | Presumed |  | 5 | 4 | 9 | Manage
78 Tilldrone Ave | External | Roof | Flue | 2m | Presumed |  | 6 | 0 | 6 | Manage
78 Tilldrone Ave | External | Wall | Cable Guide | 2 | Presumed |  | 6 | 0 | 6 | Manage
80 Tillydrone Ave | Ground | Vestibule | Adhesive to floor | 3m2 | Chrysotile |  | 3 | 5 | 8 | Manage
80 Tillydrone Ave | Ground | Hall | Floor tiles | 8m2 | Chrysotile |  | 3 | 5 | 8 | Manage
80 Tillydrone Ave | Ground | Bathroom | Floor tiles | 3m2 | Chrysotile |  | 3 | 5 | 8 | Manage
80 Tillydrone Ave | Ground | Living room | Floor tiles | 20m2 | Chrysotile |  | 3 | 5 | 8 | Manage
80 Tillydrone Ave | Ground | Dining Room | Floor tiles | 12m2 | Chrysotile |  | 3 | 5 | 8 | Manage
80 Tillydrone Ave | Ground | Kitchen | Floor tiles | 8m2 | Chrysotile |  | 3 | 5 | 8 | Manage
80 Tillydrone Ave | External | Shed | Roof Panels | 20m2 | Presumed |  | 5 | 4 | 9 | Manage
80 Tillydrone Ave | External | Wall | cowl | 1m | Presumed |  | 6 | 0 | 6 | Manage
80 Tillydrone Ave | External | Roof | Flue | 2m | Presumed |  | 4 | 3 | 7 | Manage
84 Tillydrone Ave | Ground | Hall | Floor tiles | 6m2 | Chrysotile |  | 3 | 5 | 8 | Manage
84 Tillydrone Ave | Ground | Living room | Floor tiles | 20m2 | Chrysotile |  | 3 | 5 | 8 | Manage
84 Tillydrone Ave | Ground | Dining Room | Floor tiles | 15m2 | Chrysotile |  | 3 | 5 | 8 | Manage
84 Tillydrone Ave | Ground | Kitchen | Floor tiles | 8m2 | Chrysotile |  | 3 | 5 | 8 | Manage
84 Tillydrone Ave | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
84 Tillydrone Ave | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
84 Tillydrone Ave | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
84 Tillydrone Ave | Ground | Toilet | Floor tiles | 3m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Hall | Floor tiles | 8m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Kitchen | Adhesive to floor | 6m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Kitchen | Sink pad | 1m2 | Presumed |  | 5 | 5 | 10 | Manage
86 Tillydrone Ave | Ground | Cupboard | Adhesive to floor | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Cupboard | Adhesive to floor | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Cupboard | Adhesive to floor | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Dining Room | Floor tiles | 12m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Living room | Floor tiles | 20m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Toilet | Floor tiles | 2m2 | Chrysotile |  | 3 | 5 | 8 | Manage
86 Tillydrone Ave | Ground | Cupboard | Floor tiles | 2m2 | Chrysotile |  | 3 | 5 | 8 | Manage
4 Wrights' & Coopers' | Ground | Kitchen | Sink pad | 1m2 | Chrysotile |  | 3 | 5 | 8 | Manage
Balgownie Home Farm | Ground | Bathroom | Floor Covering | 4m2 | Chrysotile |  | 3 | 4 | 7 | Manage
Balgownie Home Farm | Ground | Bathroom | Toilet cistern | 1m2 | Amosite, Chrysotile |  | 3 | 6 | 9 | Manage
Balgownie Home Farm | External | Roof | Roof Panels | 16m2 | Chrysotile |  | 4 | 1 | 5 | Manage
D Strathcona | Ground | Entrance | Cement Flue | 3m2 | Presumed |  | 4 | 5 | 9 | Manage
Hope Farm Cottage | External | Store | Roof Panels | 8m2 | Chrysotile |  | 3 | 4 | 7 | Manage
Hope Farm Cottage | External | Garage | Roof Panels | 10m2 | Chrysotile |  | 3 | 4 | 7 | Manage
North Lodge Balgownie | Ground | store | Cement shelves | 2 | Chrysotile |  | 4 | 4 | 8 | Manage
North Lodge Balgownie | External | Shed | roof & wall panels | 16 | Chrysotile |  | 4 | 3 | 7 | Manage
IF A PROPERTY IS NOT LISTED HERE, IT HAS BEEN SURVEYED AND NO ASBESTOS HAS BEEN DETECTED OR IT HAS BEEN SOLD OR DEMOLISHED
Sold Properties
Ardtornish | External | Garage | Roof Panels | 50m2 | Presumed | Sold 27/01/20
Greenburn House | Ground | Kitchen | Sink pad | 1m2 | Chrysotile | Sold 27/09/19
Greenburn House | Ground | Utility Room | Sink pad | 1m2 | Chrysotile
Greenburn House | External | roof | Soffits | 40m | Chrysotile
Greenburn House | External | Garage | Wall Panels | 40m2 | Chrysotile
Greenburn House | External | Outbuilding | Roof Panels | 16m2 | Chrysotile
Landers House | External | Garage | Roof Panels | 18m2 | Chrysotile | Sold 27/09/19
Landers House | External | Garage | Walls | 16m2 | Chrysotile
Landers House | External | Store | Wall Panels | 16m2 | Chrysotile
Landers House | Ground | Electrical Cupboard | Electrics | 4 | Presumed
Landers House | Ground | hall | Textured coating to ceiling | 13m2 | Chrysotile
Landers House | External | Store | Roof Panels | 18m2 | Chrysotile
Landers House | First | Hall | Textured coating to ceiling | 13m2 | Chrysotile
Swaarbeck House | External | Garage | Corrugated cement wall paneling | 40m2 | Chrysotile | Sold 28/02/20
5 Eastside Gardens | Ground | Kitchen | Sink Pad | 1m2 | Chrysotile | Sold 11/12/20
5 Eastside Gardens | First | Loft | Firebreak | 5m2 | Amosite, Chrysotile
5 Eastside Gardens | External | roof | Undercloak | 5m2 | Chrysotile
5 Eastside Gardens | External | Garage | Roof Panels | 70m2 | Chrysotile
7 Eastside Gardens | Ground | Kitchen | Sink Pad | 1m2 | Chrysotile | Sold 30/11/20
7 Eastside Gardens | External | Roof | Undercloak | 20m | Amosite, Chrysotile
1 Walton Rd | Ground | Hall | Floor tiles | 8m2 | Chrysotile | Sold 23/04/21
1 Walton Rd | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile
1 Walton Rd | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile
1 Walton Rd | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile
1 Walton Rd | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile
1 Walton Rd | Ground | Bedroom | Floor tiles | 16m2 | Chrysotile
1 Walton Rd | Ground | Bedroom | Floor tiles | 16m2 | Chrysotile
1 Walton Rd | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile
1 Walton Rd | Ground | Living Room | Textured coating | 20m2 | Presumed
1 Walton Rd | Ground | Cupboard | Floor tiles | 1m2 | Chrysotile
1 Walton Rd | External | Garage | Roof Panels | 10m2 | Chrysotile
1 Walton Rd | External | Shed | Roof Panels | 2m2 | Chrysotile
2 Walton Road | Ground | Kitchen | Sink Pad | 1m2 | Chrysotile | Sold 14/05/21
2 Walton Road | External | Garage | Roof Panels | 10m2 | Chrysotile
2 Walton Road | Attic | Loft | Loose lying panel | 1m2 | Chrysotile
4 Walton Rd | Ground | Bathroom | Toilet cistern | 1m2 | Crocidolite, Amosite | Sold 25/06/21
4 Walton Rd | External | Garrage | Roof Panels | 10m2 | Chrysotile
5 Walton Rd | External | Garage | Roof Panels | 10m2 | Chrysotile | Sold 20/02/20
6 Walton Rd | External | Roof | Corrugated roof | 10m2 | Chrysotile | Sold 20/02/20
8 Walton Rd | Ground | Kitchen | Sink pad | 1m2 | Chrysotile | Sold 17/06/12
8 Walton Rd | External | Garage | Corrugated roof | 10m2 | Chrysotile
8 Walton Rd | Shed | Garage | Corrugated roof | 10m2 | Chrysotile
8 Walton Rd | External | Garden | Debris | 1m2 | Chrysotile
8 Walton Rd | External | Garden | Debris | 1m2 | Chrysotile
8 Walton Rd | External | Garden | Garden edging | 2m | Chrysotile
10 Eastside Gardens | External | Roof | Undercloak | 20m | Chrysotile | Sold 28/05/21
1 College Bounds | Ground | Hall | Floor tiles | 10m2 | Chrysotile | Sold 29/01/21
1 College Bounds | Ground | Kitchen | Floor tiles | 1m2 | Chrysotile
1 College Bounds | Ground | Living room | Floor tiles | 24m2 | Chrysotile
1 College Bounds | Ground | Cupboard | Floor tiles | 2m2 | Chrysotile
1 College Bounds | Ground | Cupboard | Floor tiles | 2m2 | Chrysotile
1 College Bounds | Ground | Cloak Room | Floor tiles | 4m2 | Chrysotile
1 College Bounds | Ground | Toilet | Cistern | 1m2 | Chrysotile
1 College Bounds | First | Toilet | Cistern | 1m2 | Chrysotile
1 College Bounds | Ground | Cupboard | Floor tiles |  | Chrysotile
1 College Bounds | Loft |  | Limited access

## ST MARYS
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
|  | Lower ground | B01A | AIB Beam cladding on structural steel | 20 | Amosite/chrysotile | Encapsulated and labelled | 5 | 3 | 8 | Manage & reinspect
|  | Lower ground | B01A | AIB Beam cladding on structural steel | 2 | Amosite/chrysotile | Encapsulated and labelled | 5 | 3 | 8 | Manage & reinspect
|  | Lower ground | B01A | Panels over door | 1 | Amosite/chrysotile | Encapsulated and labelled | 5 | 3 | 8 | Manage & reinspect
|  | Lower ground | B01B | AIB Beam cladding on structural steel | 12 | Amosite/chrysotile | Encapsulated and labelled | 5 | 3 | 8 | Manage & reinspect
|  | Lower ground | B04 | Under sink mat | 2 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
|  | Lower ground | B07 | Ceiling artex | 2 | Chrysotile |  | 3 | 6 | 9 | Manage & reinspect
|  | Lower ground | B08 | Ceiling artex | 20 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B09 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B10 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B11 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B12 | Ceiling artex | 10 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B13 | Ceiling artex | 25 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B14 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B15 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B16 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B17 | Ceiling artex | 30 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B18 | Ceiling artex | 25 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B19 | Ceiling artex | 5 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B19a | Ceiling artex | 10 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B20A | Ceiling artex | 20 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B21 | Ceiling artex | 5 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B22 | Ceiling artex | 30 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B22A | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B24 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B25 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B26 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Lower ground | B29 | Stramit board | 12 | Amosite |  | 9 | 6 | 15 | Manage & reinspect
|  | Lower ground | B30 | Stramit board | 12 | 10 |  | 9 | 6 | 15 | Manage & reinspect
|  | Lower ground | B31 | Stramit board | 12 | 12 |  | 9 | 6 | 15 | Manage & reinspect
|  | Lower ground | B32 | Stramit board | 12 | 8 |  | 9 | 6 | 15 | Manage & reinspect
|  | Lower ground | B33 | Stramit board | 12 | 6 |  | 9 | 6 | 15 | Manage & reinspect
|  | Lower ground | B37 | Black WC Cistern | 1 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
|  | Lower ground | B37 - Ceiling void | AIB Beam cladding on structural steel | 0.5 | Amosite/chrysotile | Encapsulated by Pyeroy Jan 09 | 5 | 2 | 7 | Manage & reinspect
|  | Lower ground | Corridor 3 | Ceiling artex | 40 | Chrysotile |  | 3 | 6 | 9 | Manage & reinspect
|  | Lower ground | Externally accessed plant room | Gasket on pipework | 2 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
|  | Lower ground | Plant room | Gasket on pipework adjacent motor | 1 | Chrysotile |  | 4 | 4 | 8 | Manage & reinspect
|  | Lower ground | Stairwell 6 | AIB Beam cladding on structural steel | 2 | Amosite/chrysotile | Encapsulated and labelled | 5 | 3 | 8 | Manage & reinspect
|  | Lower ground | Store 6 (Fan room off B01) | Boxing over door | 2 | Amosite/chrysotile | Encapsulated by Pyeroy Jan 09 | 5 | 4 | 9 | Manage & reinspect
|  | Lower ground | Switch room | AIB Beam cladding on structural steel | 6 | Amosite/chrysotile | Encapsulated by Pyeroy Jan 09 - Boxing in undercroft encapsulated by Cape Sep 09 | 5 | 6 | 11 | Manage & reinspect
|  | Lower ground | Switch room | Rope seal on duct | 2 | Chrysotile | Encapsulated by Pyeroy Jan 09 | 4 | 6 | 10 | Manage & reinspect
|  | Ground | Corridor | AIB Beam cladding on structural steel | 20 | Amosite/chrysotile | Presumed within ceiling void | 5 | 5 | 10 | Manage & reinspect
|  | Ground | Corridor 2 | White stair nosing | 0.5 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
|  | Ground | Corridor 3 | White stair nosing | 0.5 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
|  | Ground | G03-within ceiling void | AIB Beam cladding on structural steel | 20 | Amosite/chrysotile | Beams over suspended ceiling encapsulated by Rhodar Dec 11 | 5 | 5 | 10 | Manage & reinspect
|  | Ground | G05 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G06 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G07 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G08 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G09 | Ceiling artex | 20 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G10 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G11 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G12 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G13 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G14 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | G15 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | Ground | Link corridor | Ceiling artex | 60 | Chrysotile |  | 3 | 6 | 9 | Manage & reinspect
|  | First | Corridor | AIB Beam cladding on structural steel | 40 | Amosite/chrysotile | Presumed within ceiling void | 6 | 5 | 11 | Manage & reinspect
|  | First | Room 101 | AIB Beam cladding on structural steel | 10 | Amosite/chrysotile | Presumed within ceiling void | 6 | 5 | 11 | Manage & reinspect
|  | First | Room 102 | AIB Beam cladding on structural steel | 10 | Amosite/chrysotile | Presumed within ceiling void | 6 | 5 | 11 | Manage & reinspect
|  | First | Room 103 | AIB Beam cladding on structural steel | 10 | Amosite/chrysotile | Presumed within ceiling void | 6 | 5 | 11 | Manage & reinspect
|  | First | Room 105 Ceiling void | AIB Beam cladding on structural steel | 40 | Amosite/chrysotile | Beams over suspended ceiling encapsulated by Rhodar Dec 11 | 5 | 5 | 10 | Manage & reinspect
|  | First | Room 109 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 110 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 111 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 112 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 113 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 114 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 115 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 116 | Ceiling artex | 15 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room 117 Lecture room | Ceiling artex | 40 | Chrysotile |  | 3 | 7 | 10 | Manage & reinspect
|  | First | Room104 | AIB Beam cladding on structural steel | 10 | Amosite/chrysotile | Presumed within ceiling void | 6 | 5 | 11 | Manage & reinspect
|  | First | Stairwell 1 | Ceiling artex | 20 | Chrysotile |  | 3 | 6 | 9 | Manage & reinspect
|  | Second | Corridor 1 | Mastic seal to windows | 10 | Chrysotile |  | 4 | 4 | 8 | Manage & reinspect
|  | External | Pitched roof over main entrance | Flue & flue cap | 2 | Chrysotile | Flue likely to rise from former ladies toilet and may be present within wall cavity | 4 | 0 | 4 | Manage & reinspect
|  | External | Roof | Soffits | 100 | Amosite/chrysotile |  | 7 | 1 | 8 | Manage & reinspect
|  | External | Roof | Cement promenade tiles | 20 | Chrysotile | Sampled Nov 2018 - Tremolite | 4 | 1 | 5 | Manage & reinspect
|  | All | Stairwell 2 | Ceiling artex | 10 | Chrysotile |  | 3 | 6 | 9 | Manage & reinspect
|  | All | Stairwell 4 | White stair nosing | 2 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
Updated March 2025

## TAYLOR
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Taylor | Block A 2nd Floor | Internal roof eaves (Accessed via A37 and others) | Seal to cast iron drainpipes | 5 | Amosite | Presumed to be present in all similar locations within this building | 6 | 2 | 8 | Manage & reinspect
| Taylor | Block C Lower Ground | Main cleaners store | Pipe hanger packers | 1 | Chrysotile |  | 5 | 5 | 10 | Manage & reinspect
| Taylor | Block C Lower Ground | Main Switch room | Woven textiles | 1 | Presumed | Distribution board | 6 | 2 | 8 | Manage & reinspect
| Taylor | Block C Lower Ground | Former car park attendants bothy | Pipe hanger packers | 1 | Chrysotile |  | 5 | 4 | 9 | Manage & reinspect
| Taylor | Block C 3rd Floor | Internal roof eaves | Seal to cast iron drainpipes | 5 | Amosite | Presumed to be present in all similar locations within this building | 6 | 2 | 8 | Manage & reinspect
| Taylor | Block D Ground | Duct | Pipe hanger packers | 1 | Chrysotile |  | 5 | 4 | 9 | Manage & reinspect
| Taylor | Block D 2nd Floor | Roof eaves | Seal to cast iron drainpipes | 5 | Amosite | Presumed to be present in all similar locations within this building | 6 | 2 | 8 | Manage & reinspect
| Taylor | Block E 2nd Floor | Roof eaves | External soffits | 5 | Amosite | Presumed due to limited access | 6 | 0 | 6 | Manage & reinspect
Updated March 2025

## UNIVERSITY OFFICE
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| University Office | Ground | Room 046 Electrical cupboard space 1080 | Distribution boards | 1 | presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| University Office | Ground | Link corridor electric cupboard Space 1058 | Distribution boards | 1 | presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| University Office | Ground | Room 001 Electrical cupboard Space 1004 | Distribution boards | 1 | presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| University Office | Ground | External plant room | Distribution boards | 1 | presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| University Office | First | Room 122 Electrical cupboard | Distribution boards | 1 | presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| University Office | First | Room 120 Electrical Cupboard | Distibution board | 1 | presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| University Office | First | Kitchen | Under sink mat | 1 | Chrysotile |  | 2 | 3 | 5 | Manage & reinspect | Medium | 10-14 | 6 Months
| University Office | First | Link corridor electric cupboard Space 1058 | Distibution board | 1 | presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| University Office | Roof | Lift motor room | Brake pads | 1 | Chrysotile | Needs sampled | 3 | 4 | 7 | Manage & reinspect
[12 empty] | Low | 1-9 | 12 Months
Updated March 2025

## WAVELL
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| Wavell | Ground | Stairwell A | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Ground | Stairwell B | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Ground | Stairwell C | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Ground | Stairwell D | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | First | Stairwell A | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | First | Stairwell B | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | First | Stairwell C | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | First | Stairwell D | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Second | Stairwell A | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Second | Stairwell B | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Second | Stairwell C | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Second | Stairwell D | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Third | Stairwell A | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Third | Stairwell B | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Third | Stairwell C | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | Third | Stairwell D | Black panel below window | 1 | Chrysotile |  | 4 | 3 | 7 | Manage & reinspect
| Wavell | All | Stairs | Stair nosings |  | Chrysotile |  | 6 | 3 | 9 | Manage & reinspect
| Wavell | All bathrooms | toilets | All cisterns and seats |  | Amosite |  | 2 | 3 | 5 | Manage & reinspect
| Fyfe House March 2024 | Ground | Fire doors | Mastic / Putty | 10 | Chrysotile (presumed) | Fyfe doors were tested in March 2024 and result was positive. | 4 | 3 | 7 | Manage & Reinspect
Updated March 2025

## WILLIAM GUILD
Survey Ref | Survey | Floor | Area | Item | Extent | Asbestos | Comments | MA Total | PA TOTAL | TOTAL RISK SCORE | Action Required
| William Guild 2017 | Basement | L004 Cupboard | Ceiling & wall panelling | 6 | Amosite/Chrysotile | Encapsulated by Cape 5/12/09 | 4 | 3 | 7 | Manage & reinspect
| William Guild 2017 | Basement | L001 Cupboard | Ceiling & wall panelling | 6 | Amosite/Chrysotile | Encapsulated by Cape 5/12/09 | 4 | 3 | 7 | Manage & reinspect
| William Guild 2017 | Basement | Main service duct from plant room | Gasket on main steam pipe at W end of duct | 2 | Chrysotile |  | 3 | 0 | 3 | Manage & reinspect
| William Guild 2017 | Basement | Main service duct from plant room | Flange sleeve material to main steamline & condensate return | 6 | Chrysotile |  | 3 | 0 | 3 | Manage & reinspect
| William Guild 2017 | Basement | Main Plant room | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Ground | ALT projector room | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Ground | East plant room | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Ground | West plant room | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Ground | North electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Ground/First | Stairs L2 | Grey panelling around windows | 10 | Amosite/ Chrysotile | Encapsulated by Pyeroy Jan 09. Labelled | 5 | 5 | 10 | Manage & reinspect
| William Guild 2017 | Ground/First | Stairs L1 | Grey panelling around windows | 12 | Amosite/ Chrysotile | Encapsulated by Pyeroy Jan 09. Labelled | 5 | 4 | 9 | Manage & reinspect
| William Guild 2017 | First | East electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | First | West Electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Second | East electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Second | West Electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Second | West block corridor | Woven material to HVAC ducting flange joint |  | Chrysotile | new entry Feb 17 | 5 | 2 | 7 | Manage & reinspect
| William Guild 2017 | Third | East electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Third | West Electrical cupboard | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Fourth | Tank room | Gaskets on pipes | 2 | Chrysotile |  | 2 | 4 | 6 | Manage & reinspect
| William Guild 2017 | Roof | Lift plant room | Distribution board | 1 | Presumed | Needs sampled | 6 | 2 | 8 | Manage & reinspect
| William Guild 2017 | Behind all radiators | East wing all floors | Grey panelling around windows | 60 | Chrysotile | Encapsulated and boxed in | 4 | 2 | 6 | Unable to see to manage
Updated March 2025

## ZOOLOGY
Survey Ref | Survey | Floor | Area | Item | Extent | Comments | Asbestos | Material Risk | Priority Risk | Total Risk Score | Action Required
| Zoology 2021 | Basement | Lift Corridor Ceiling void | Spray coating to beams | 10m run |  | Amosite | 7 | 5 | 12 | Manage & reinspect
| Zoology 2021 | Basement | B21 Natural history centre Wall | Insulating board panels | 3.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B21 Natural history centre Horizontal cladded beams | Insulating board | 75.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B21 Natural history centre Vertical cladded beams | Insulating board | 8m run |  | Amosite | 6 | 4 | 10 | Manage & reinspect
| Zoology 2021 | Basement | B47 Store Throughout |  | Non/a |  | No Access | 9 | 0 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B20 Office Wall | Insulating board panels | 8.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B20 Office Horizontal cladded beams | Insulating board | 5m run |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 1 Ceiling void | Spray coating to beams | 2m run |  | Amosite | 7 | 5 | 12 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 2 Ceiling void | Spray coating to beams | 4m run |  | Amosite | 7 | 5 | 12 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 2 Wall | Insulating board panel | 4.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 3 Horizontal cladded beams | Insulating board | 1.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 3 Horizontal cladded beams | Insulating board | 1m run |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 3 Within electric cupboard riser hatch | Insulating board panel | 0.50 m2 |  | Amosite | 6 | 5 | 11 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 3 Wall | Insulating board panels above door | 1.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B23 Tank Store Wall | Insulating board panels | 3.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B23 Tank Store Horizontal cladded beams | Insulating board | 6m run |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B43 Museum Store Horizontal beam cladding | Insulating board | 6m run |  | Amosite | 6 | 4 | 10 | Manage & reinspect
| Zoology 2021 | Basement | B42 Electrical Cupboard Horizontal beam cladding | Insulating board | 1m run |  | Amosite | 6 | 4 | 10 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 4 Door headers and panels | Insulating board | 8.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 5 Panel above door | Insulating board panels | 1.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 6 Ceiling void | Spray coating to beams | 7m run |  | Amosite | 7 | 5 | 12 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 7 Packing between brick and beam | Insulating board | 4m run |  | Amosite | 6 | 1 | 7 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 7 Insulating board debris on ceiling tiles | Insulating board | 1.00 m2 |  | Amosite | 10 | 5 | 15 | Manage & reinspect
| Zoology 2021 | Basement | Stairwell Packing between brick and beam | Insulating board | 1m run |  | Amosite | 6 | 1 | 7 | Manage & reinspect
| Zoology 2021 | Basement | B42 Electrical Cupboard Within fuse boxes | Woven Materials | small amounts |  | Asbestos | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B33 Laboratory Lining within oven | Insulating board | 1 item |  | Asbestos | 6 | 4 | 10 | Manage & reinspect
| Zoology 2021 | Basement | Electrical Cupboard Electrics | Woven materials within electrical boxes | 4m run |  | Asbestos | 7 | 3 | 10 | Manage & reinspect
| Zoology 2021 | Basement | B43 Museum Store Floor | Light blue floor tiles and adhesive | 45.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B42 Electrical Cupboard Floor | Light blue floor tiles and adhesive | 4.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B51 Museum Floor | Floor tiles below carpet | 100.00 m2 |  | Chrysotile | 2 | 6 | 8 | Manage & reinspect
| Zoology 2021 | Basement | Corridor 4 Pipework | Woven packing within pipe joint | 1m run |  | Chrysotile | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B28 Office Floor | Floor tiles and adhesive below carpet | 12.00 m2 |  | Chrysotile | 2 | 4 | 6 | Manage & reinspect
| Zoology 2021 | Basement | B35 Cleaners Store Floor | Floor tiles and adhesive | 4.00 m2 |  | Chrysotile | 2 | 5 | 7 | Manage & reinspect
| Zoology 2021 | Basement | B38 Cleaners Store Floor | Floor tiles and adhesive | 4.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Basement | B30 Store Floor | Floor tiles and adhesive | 15.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B34 Lab office Floor | Floor tiles and adhesive | 4.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B03 teaching Lab Insulating board lining oven | Insulating board | small amounts |  | Chrysotile | 4 | 3 | 7 | Manage & reinspect
| Zoology 2021 | Basement | B04 Teaching Lab Store Insulating board lining oven | Insulating board Small Amounts | small amounts |  | Chrysotile | 4 | 3 | 7 | Manage & reinspect
| Zoology 2021 | Basement | Electrical Cupboard Floor | Floor tiles and adhesive | 2.00 m2 |  | Chrysotile | 3 | 2 | 5 | Manage & reinspect
| Zoology 2021 | Basement | B11 Tech Lab Lining within oven | Cement | 0.50 m2 |  | Chrysotile | 2 | 4 | 6 | Manage & reinspect
| Zoology 2021 | Basement | B11 Tech Lab Seal around door | Rope seal around door | 1m run |  | Chrysotile | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B13 Teaching Lab Insulating board lining oven | Insulating board Small Amounts | small amounts |  | Chrysotile | 4 | 3 | 7 | Manage & reinspect
| Zoology 2021 | Basement | B14 Teaching Lab Insulating board lining oven | Insulating board Small Amounts | small amounts |  | Chrysotile | 4 | 3 | 7 | Manage & reinspect
| Zoology 2021 | Basement | B27 A Floor | Bitumen adhesive | 2.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B27 C Floor | Bitumen adhesive | 2.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B27 D Floor | Bitumen adhesive | 8.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B27 E Floor | Bitumen adhesive | 8.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Basement | Lift corridor Throughout | No Access N/A | Non/a |  | No Access | 9 | 0 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B50 Riser Throughout | No Access N/A | Non/a |  | No Access | 9 | 0 | 9 | Manage & reinspect
| Zoology 2021 | Basement | B52 Store Throughout | No Access N/A | Non/a |  | No Access | 9 | 0 | 9 | Manage & reinspect
| Zoology 2021 | Basement | External Store Throughout | No Access N/A | Non/a |  | No Access | 9 | 0 | 9 | Manage & reinspect
| Zoology 2021 | Ground | Stairwell Ceiling void | Spray coating to beams | 1m run |  | Amosite | 7 | 5 | 12 | Manage & reinspect
| Zoology 2021 | Ground | Projector Room Ceiling | Insulating board | 2.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Ground | Projector Room Walls | Insulating board | 6.00 m2 |  | Amosite | 5 | 4 | 9 | Manage & reinspect
| Zoology 2021 | Ground | G20 Cleaners Office Cladding to beams | Insulating board | 3m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Ground | Service Riser Cladding to beams | Insulating board Small Amounts | small amounts |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Ground | Corridor 10 Cladding to beams | Insulating board | 7m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G23 Plant Room Cladding to beams | Insulating board | 3m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G24 Plant Room Spray coating to beam | Spray coating | 12m run |  | Amosite | 7 | 5 | 12 | Manage & reinspect
| Zoology 2021 | Ground | G24 Plant Room Cladding to beams | Insulating board | 14m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Ground | Walkway Cladding to beams | Insulating board Small Amounts | small amounts |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Ground | Service riser Cladding to beams | Insulating board | 2m run |  | Amosite | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Ground | G17 Plant room Cladding to beams | Insulating board | 6m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Ground | 114 Office Insulating board | Within concrete | 2.00 m2 |  | Amosite | 6 | 0 | 6 | Manage & reinspect
| Zoology 2021 | Ground | Corridor Ceiling Void | Insulating board | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Ground | Corridor 3 Fuse box | Paper lining within fuses Throughout | fuses throughout |  | Asbestos | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Ground | Main Lobby Ceiling void | Insulating board cladded beams | 8m run |  | Asbestos | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | Ground | G24 Plant Room Pipework joints | Gaskets to pipework Throughout | pipework throughout |  | Asbestos | 5 | 1 | 6 | Manage & reinspect
| Zoology 2021 | Ground | G02 Plant Room Fuse boxes | Woven materials within electrics Small Amounts | small amounts |  | Asbestos | 7 | 1 | 8 | Manage & reinspect
| Zoology 2021 | Ground | G19 Museum Floor | Floor tiles and adhesive | 14.00 m2 |  | Chrysotile | 2 | 5 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G21 Computer Room Floor | Bitumen screed below floor | 24.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G22 Mail Room Floor | Floor tile and adhesive below carpet | 8.00 m2 |  | Chrysotile | 2 | 4 | 6 | Manage & reinspect
| Zoology 2021 | Ground | Reception/secretariat Floor | Bitumen adesive below carpet | 44.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G34 Office Floor | Bitumen adesive below carpet | 4.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G35 Office Floor | Bitumen adesive below carpet Small Amounts | small amounts |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G36 Office Floor | Bitumen adesive below carpet | 4.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G37 Office Floor | Bitumen adesive below carpet | 4.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G38 Store Floor | Bitumen adesive below carpet | 4.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G39 Store Floor | Bitumen adesive below carpet | 2.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G40 Computer Room Floor | Bitumen adesive below carpet | 18.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Ground | G41 Server Room Floor | Floor tiles and adhesive | 6.00 m2 |  | Chrysotile | 3 | 3 | 6 | Manage & reinspect
| Zoology 2021 | Ground | G17 Plant Room Within Loose electrics box | Cement ark shield Small Amounts | small amounts |  | Chrysotile | 3 | 2 | 5 | Manage & reinspect
| Zoology 2021 | Ground | G17 Plant Room Electrics box | Woven seal on loose electrics box Small Amounts | small amounts |  | Chrysotile | 5 | 6 | 11 | Manage & reinspect
| Zoology 2021 | Ground | G02 Plant Room Pipework | Gaskets to pipe joints Throughout | joints throughout |  | Chrysotile | 3 | 2 | 5 | Manage & reinspect
| Zoology 2021 | Ground | G16 Plant Room Floor | Woven material Small Amounts | small amounts |  | Chrysotile | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | Lift Corridor Beamwork | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | Lift Corridor between brick work and ducting | Insulating board Small Amounts | small amounts |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | Corridor Beamwork | Insulating board Small Amounts | small amounts |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 101 Plant Room Beamwork | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 102 Office within concrete | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 103 Office Within Concrete | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 104 Lab Within concrete | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 111 Duct Room Beamwork | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 115 Lab Between concrete | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | Riser Beamwork | Insulating board | 1m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 123 Office Beamwork | Insulating board | 2m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 123 Office Beamwork | Insulating board Small Amounts | small amounts |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 118 Office Beamwork | Insulating board Small Amounts | small amounts |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | First | 103 Office Floor | Bitumen adhesive below carpet | 6.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | First | 111 Duct Room Floor | Floor tiles and adhesive | 6.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Second | 251 Circulation Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Second | 251 Circulation Ceiling void on ducts | Insulating board debris Throughout | debris throughout |  | Amosite | 9 | 3 | 12 | Manage & reinspect
| Zoology 2021 | Second | 252 Corridor Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 4 | 3 | 7 | Manage & reinspect
| Zoology 2021 | Second | 201 Riser Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Second | 202 Office Ceiling Void | Insulating board | 2.00 m2 |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Second | 203 Lab on Beam | Insulating board debris Small Amounts | boardsmall amounts |  | Amosite | 9 | 3 | 12 | Manage & reinspect
| Zoology 2021 | Second | 205 Office Ceiling Void | Insulating board | 2.00 m2 |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Second | 207 208 Sitting area Ceiling Void | Insulating board to beams Small Amounts | small amounts |  | Amosite | 4 | 3 | 7 | Manage & reinspect
| Zoology 2021 | Second | 209 Office Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Second | 255 Stairwell Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Second | 255 Stairwell Ceiling void | Insulating board to timbers Small Amounts | small amounts |  | Amosite | 9 | 5 | 14 | Manage & reinspect
| Zoology 2021 | Second | 255 Stairwell Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 4 | 3 | 7 | Manage & reinspect
| Zoology 2021 | Second | Riser on Beam | Insulating board debris | 2.00 m2 |  | Amosite | 9 | 3 | 12 | Manage & reinspect
| Zoology 2021 | Second | Riser Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Second | 250 Corridor Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Second | 202 Office Ceiling Void | Insulating board | 2m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Second | 206 Office Ceiling Void | Insulating board | 4m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Second | 214 Ceiling Void | Insulating board | 1m run |  | Amosite | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | Second | 205 Office Floor | Below carpet | 6.00 m2 |  | Chrysotile | 2 | 6 | 8 | Manage & reinspect
| Zoology 2021 | Second | 209 Office Floor | Below carpet | 6.00 m2 |  | Chrysotile | 2 | 6 | 8 | Manage & reinspect
| Zoology 2021 | Second | 210 Storage Floor | Bitumen adhesive | 1.00 m2 |  | Chrysotile | 2 | 6 | 8 | Manage & reinspect
| Zoology 2021 | Second | 215 Office Floor | Below carpet | 6.00 m2 |  | Chrysotile | 2 | 6 | 8 | Manage & reinspect
| Zoology 2021 | Third | Stairwell Ceiling Void | Insulating board Small Amounts | small amounts |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Third | 301 Riser Ceiling Void | Insulating board | 2.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Third | 302 Office Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 5 | 6 | 11 | Manage & reinspect
| Zoology 2021 | Third | 303 Office Ceiling Void | Insulating board to beams | 2.00 m2 |  | Amosite | 5 | 6 | 11 | Manage & reinspect
| Zoology 2021 | Third | 304 Office Ceiling Void | Insulating board to beams | 2m run |  | Amosite | 5 | 6 | 11 | Manage & reinspect
| Zoology 2021 | Third | 311 Lab Ceiling Void | Insulating board | 2m run |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Third | 318 Male Toilets Ceiling Void | Insulating board to beams | 2m run |  | Amosite | 5 | 6 | 11 | Manage & reinspect
| Zoology 2021 | Third | 301 Riser Floor | Floor tile remanants on the floor Small Amounts | thesmall amounts |  | Chrysotile | 3 | 3 | 6 | Manage & reinspect
| Zoology 2021 | Fourth | 401 Riser Beams | Insulating board to beams | 2m run |  | Amosite | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 401 Riser Metal work | Insulating board residues to metal work Small Amounts | metalsmall amounts |  | Amosite | 9 | 2 | 11 | Manage & reinspect
| Zoology 2021 | Fourth | 402 Lab Ceiling Void | Insulating board | 1.00 m2 |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | Fourth | 403 Lab Ceiling Void | Insulating board | 1m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | Fourth | 407 Office Ceiling Void | Insulating board panel to ceiling | 1.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 408 Office Ceiling Void | Insulating board panel to ceiling | 1.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 411 Office Ceiling Void | Insulating board | 1m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | Fourth | Stairwell Beams | Insulating board to beams Small Amounts | small amounts |  | Amosite | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 414 Store Beams | Insulating board to beams Small Amounts | small amounts |  | Amosite | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 415 Lab Beams | Insulating board to beams | 2m run |  | Amosite | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 419 Office Ceiling Void | Insulating board | 1board 1.00 m2 |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | Fourth | 420 Female Toilets Ceiling Void | Insulating board panel to ceiling | 1ceiling 1.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 422 Office Ceiling Void | Insulating board | 1.00 m2 |  | Amosite | 6 | 1 | 7 | Manage & reinspect
| Zoology 2021 | Fourth | 422 Office Ceiling Void | Insulating board | 1m run |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | Fourth | Corridor Beams | Insulating board to beams Small Amounts | small amounts |  | Amosite | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 423 Lab Beams | Insulating board to beams | 1m run |  | Amosite | 7 | 2 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 423 Lab Ceiling Void | Insulating board panel to ceiling | 1.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 427 Lab Ceiling Void | Insulating board to beams Small Amounts | small amounts |  | Amosite | 6 | 2 | 8 | Manage & reinspect
| Zoology 2021 | Fourth | 417 Office Ceiling Void | Insulating board panel to ceiling | 1.00 m2 |  | Amosite | 6 | 3 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 401 Riser Floor | Floor tiles and adhesive | 1.00 m2 |  | Chrysotile | 3 | 4 | 7 | Manage & reinspect
| Zoology 2021 | Fourth | 415 Office Floor | Bitumen adhesive | 4.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 416 Office Floor | Bitumen adhesive | 4.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Fourth | 422 Office Floor | Bitumen adhesive | 12.00 m2 |  | Chrysotile | 3 | 6 | 9 | Manage & reinspect
| Zoology 2021 | Fifth | Corridor Electrics boxes | Woven materials within electrics | 1.00 m2 |  | Asbestos | 7 | 1 | 8 | Manage & reinspect
| Zoology 2021 | Fifth | Plant Room Ducting joints | Woven materials | 1.00 m2 |  | Chrysotile | 5 | 2 | 7 | Manage & reinspect
| Zoology 2021 | External | Roof Cupboard Electrics boxes | Woven materials Small Amounts | small amounts |  | Asbestos | 5 | 6 | 11 | Manage & reinspect
| Zoology 2021 | External | Roof Brickwork | Mastic to expansion joints | 4m run |  | Asbestos | 4 | 6 | 10 | Manage & reinspect
| Zoology 2021 | External | Lift motor room Lift motor | Cement break pads Small Amounts | small amounts |  | Asbestos | 5 | 1 | 6 | Manage & reinspect
| Zoology 2021 | External | Roof Brickwork | Mastic to expansion joints Small Amounts | small amounts |  | Chrysotile | 2 | 6 | 8 | Manage & reinspect
| Zoology 2021 | External | AHU Store Floor | Bitumen roof felt to floor Throughout | floor throughout |  | Chrysotile | 2 | 6 | 8 | Manage & reinspect
Updated March 2025